{"text_format":"1","workbook":"xlsx","n_sheets":6,"sheets":["簡易入力シート","計算シート","取説","MHI(簡易版)","ルックアップ用の表","ルックアップ用の表 (2)"],"not_rendered":{"charts":0,"images":4,"macros":1,"external_links":1,"defined_names":15,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"簡易入力シート","index":0,"n_rows":35,"n_cols":34,"rows_kept":35,"cut":false,"hidden":false,"merged":[[20,4,20,5],[31,2,31,5],[16,24,16,27],[17,24,17,27],[18,24,18,27],[19,24,19,27],[21,4,21,5],[21,24,21,27],[22,4,22,5],[22,24,22,27],[23,4,23,5],[23,24,23,27],[24,4,24,5],[24,24,24,27],[25,4,25,5],[25,24,25,27],[15,4,15,5],[16,4,16,5],[4,1,4,8],[5,1,5,8],[6,1,6,8],[7,1,7,8],[1,31,1,33],[20,24,20,27],[11,2,12,3],[11,4,12,5],[11,21,12,23],[11,16,12,16],[11,19,12,19],[11,24,12,27],[14,24,14,27],[15,24,15,27],[17,4,17,5],[18,4,18,5],[19,4,19,5],[11,10,12,10],[11,13,12,13],[14,4,14,5],[26,28,26,30],[26,4,26,5],[26,24,26,27],[34,24,34,27],[27,4,27,5],[27,24,27,27],[28,4,28,5],[28,24,28,27],[31,24,32,26],[31,28,31,31],[32,2,32,5],[32,28,33,30],[33,2,33,5],[27,28,27,30],[28,28,28,30],[2,0,2,33],[22,28,22,30],[23,28,23,30],[24,28,24,30],[25,28,25,30],[11,32,12,33],[17,28,17,30],[18,28,18,30],[19,28,19,30],[20,28,20,30],[21,28,21,30],[11,28,12,31],[13,28,13,31],[14,28,14,30],[15,28,15,30],[16,28,16,30]]}
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Ver.1.1.3"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"作成日","2025-11-20"]
["R32ビル用マルチ安全対策要否判定シート（簡易版）"]
[]
[" 物件番号"]
[" 物件名"]
[" 系統番号"]
[" 系統名"]
[]
[]
[]
[null,null,"ユニット形式",null,"出荷時\n封入量",null,null,"部屋名",null,null,"部屋面積\n（㎡）",null,null,"漏えい\n想定高さ\n（ｍ）",null,null,"部屋容積\n（㎥）",null,null,"安全対策\n判定結果",null,"安全対策不要と\nなる最小面積\n（㎡）",null,null,"地下最下層の場合",null,null,null,"冷媒漏えい時\n最大濃度\n（kg/㎥）",null,null,null,"判定基準量\n(kg/㎥)"]
[null,null,null,null,null,null,null,null,"地下最下層か↓"]
["室外ユニット","①",null,"-",null,"kg",null,"-",null,null,"-",null,null,"-",null,null,"-",null,null,"-",null,null,null,null,null,null,null,null,"-"]
["室内ユニット","②",null,null,"-",null,"③",null,null,"④",null,{"$f":"IF(K15<>\"\",\"㎡\",\"\")","v":""},"⑤",null,{"$f":"IF(N15<>\"\",\"m\",\"\")","v":""},null,{"$f":"IF(OR(K15=\"\", N15=\"\"), \"\", K15*N15)","v":""},{"$f":"IF(Q15<>\"\",\"㎥\",\"\")","v":""},null,{"$f":"IF(OR(AC33=\"\",Q15=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),IF(N15=\"\",\"\",IF(ROUNDUP(AC33/Q15,4) >= MAX(0.25*0.307, 2.5*0.307^(5/4)*N15*K15^0.5/Q15),\"要\",\"不要\")),IF(ROUNDUP(AC33/Q15,4) >= 0.25*0.307,\"要\",\"不要\")))","v":""},null,null,{"$f":"IF(AC33=\"\",\"\",IFERROR(ROUNDUP(IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),MIN(AC33/N15/(0.25*0.307), (AC33/(2.5*0.307^(5/4)*N15))^2),AC33/N15/(0.25*0.307)),2),\"\"))","v":""},{"$f":"IF(W15<>\"\",\"㎡\",\"\")","v":""},{"$f":"IF(I15=\"✓\", IFERROR(IF(AC33/Q15 > IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),0.1535,0.307),\"システム見直し必要\",\"\"),\"\"),\"\")","v":""},null,null,null,{"$f":"IF(OR(AC33=\"\",Q15=\"\"),\"\",ROUNDDOWN(AC33/Q15,4))","v":""},null,null,{"$f":"IF(AC15<>\"\",\"kg/㎥\",\"\")","v":""},{"$f":"IF(OR(K15=\"\",N15=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),ROUNDDOWN(MAX(0.25*0.307, 2.5*0.307^(5/4)*N15*K15^(1/2)/(K15*N15)),3),ROUNDDOWN(0.25*0.307,3)))","v":""},{"$f":"IF(AG15<>\"\",\"kg/㎥\",\"\")","v":""}]
[null,null,null,null,"-",null,null,null,null,null,null,{"$f":"IF(K16<>\"\",\"㎡\",\"\")","v":""},null,null,{"$f":"IF(N16<>\"\",\"m\",\"\")","v":""},null,{"$f":"IF(OR(K16=\"\", N16=\"\"), \"\", K16*N16)","v":""},{"$f":"IF(Q16<>\"\",\"㎥\",\"\")","v":""},null,{"$f":"IF(OR(AC33=\"\",Q16=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),IF(N16=\"\",\"\",IF(ROUNDUP(AC33/Q16,4) >= MAX(0.25*0.307, 2.5*0.307^(5/4)*N16*K16^0.5/Q16),\"要\",\"不要\")),IF(ROUNDUP(AC33/Q16,4) >= 0.25*0.307,\"要\",\"不要\")))","v":""},null,null,{"$f":"IF(AC33=\"\",\"\",IFERROR(ROUNDUP(IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),MIN(AC33/N16/(0.25*0.307), (AC33/(2.5*0.307^(5/4)*N16))^2),AC33/N16/(0.25*0.307)),2),\"\"))","v":""},{"$f":"IF(W16<>\"\",\"㎡\",\"\")","v":""},{"$f":"IF(I16=\"✓\", IFERROR(IF(AC33/Q16 > IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),0.1535,0.307),\"システム見直し必要\",\"\"),\"\"),\"\")","v":""},null,null,null,{"$f":"IF(OR(AC33=\"\",Q16=\"\"),\"\",ROUNDDOWN(AC33/Q16,4))","v":""},null,null,{"$f":"IF(AC16<>\"\",\"kg/㎥\",\"\")","v":""},{"$f":"IF(OR(K16=\"\",N16=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),ROUNDDOWN(MAX(0.25*0.307, 2.5*0.307^(5/4)*N16*K16^(1/2)/(K16*N16)),3),ROUNDDOWN(0.25*0.307,3)))","v":""},{"$f":"IF(AG16<>\"\",\"kg/㎥\",\"\")","v":""}]
[null,null,null,null,"-",null,null,null,null,null,null,{"$f":"IF(K17<>\"\",\"㎡\",\"\")","v":""},null,null,{"$f":"IF(N17<>\"\",\"m\",\"\")","v":""},null,"","",null,{"$f":"IF(OR(AC33=\"\",Q17=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),IF(N17=\"\",\"\",IF(ROUNDUP(AC33/Q17,4) >= MAX(0.25*0.307, 2.5*0.307^(5/4)*N17*K17^0.5/Q17),\"要\",\"不要\")),IF(ROUNDUP(AC33/Q17,4) >= 0.25*0.307,\"要\",\"不要\")))","v":""},null,null,{"$f":"IF(AC33=\"\",\"\",IFERROR(ROUNDUP(IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),MIN(AC33/N17/(0.25*0.307), (AC33/(2.5*0.307^(5/4)*N17))^2),AC33/N17/(0.25*0.307)),2),\"\"))","v":""},"",{"$f":"IF(I17=\"✓\", IFERROR(IF(AC33/Q17 > IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),0.1535,0.307),\"システム見直し必要\",\"\"),\"\"),\"\")","v":""},null,null,null,{"$f":"IF(OR(AC33=\"\",Q17=\"\"),\"\",ROUNDDOWN(AC33/Q17,4))","v":""},null,null,"",{"$f":"IF(OR(K17=\"\",N17=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),ROUNDDOWN(MAX(0.25*0.307, 2.5*0.307^(5/4)*N17*K17^(1/2)/(K17*N17)),3),ROUNDDOWN(0.25*0.307,3)))","v":""},""]
[null,null,null,null,"-",null,null,null,null,null,null,"",null,null,"",null,"","",null,{"$f":"IF(OR(AC33=\"\",Q18=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),IF(N18=\"\",\"\",IF(ROUNDUP(AC33/Q18,4) >= MAX(0.25*0.307, 2.5*0.307^(5/4)*N18*K18^0.5/Q18),\"要\",\"不要\")),IF(ROUNDUP(AC33/Q18,4) >= 0.25*0.307,\"要\",\"不要\")))","v":""},null,null,{"$f":"IF(AC33=\"\",\"\",IFERROR(ROUNDUP(IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),MIN(AC33/N18/(0.25*0.307), (AC33/(2.5*0.307^(5/4)*N18))^2),AC33/N18/(0.25*0.307)),2),\"\"))","v":""},"",{"$f":"IF(I18=\"✓\", IFERROR(IF(AC33/Q18 > IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),0.1535,0.307),\"システム見直し必要\",\"\"),\"\"),\"\")","v":""},null,null,null,{"$f":"IF(OR(AC33=\"\",Q18=\"\"),\"\",ROUNDDOWN(AC33/Q18,4))","v":""},null,null,"",{"$f":"IF(OR(K18=\"\",N18=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),ROUNDDOWN(MAX(0.25*0.307, 2.5*0.307^(5/4)*N18*K18^(1/2)/(K18*N18)),3),ROUNDDOWN(0.25*0.307,3)))","v":""},""]
[null,null,null,null,"-",null,null,null,null,null,null,"",null,null,"",null,"","",null,{"$f":"IF(OR(AC33=\"\",Q19=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),IF(N19=\"\",\"\",IF(ROUNDUP(AC33/Q19,4) >= MAX(0.25*0.307, 2.5*0.307^(5/4)*N19*K19^0.5/Q19),\"要\",\"不要\")),IF(ROUNDUP(AC33/Q19,4) >= 0.25*0.307,\"要\",\"不要\")))","v":""},null,null,{"$f":"IF(AC33=\"\",\"\",IFERROR(ROUNDUP(IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),MIN(AC33/N19/(0.25*0.307), (AC33/(2.5*0.307^(5/4)*N19))^2),AC33/N19/(0.25*0.307)),2),\"\"))","v":""},"",{"$f":"IF(I19=\"✓\", IFERROR(IF(AC33/Q19 > IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),0.1535,0.307),\"システム見直し必要\",\"\"),\"\"),\"\")","v":""},null,null,null,{"$f":"IF(OR(AC33=\"\",Q19=\"\"),\"\",ROUNDDOWN(AC33/Q19,4))","v":""},null,null,"",{"$f":"IF(OR(K19=\"\",N19=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),ROUNDDOWN(MAX(0.25*0.307, 2.5*0.307^(5/4)*N19*K19^(1/2)/(K19*N19)),3),ROUNDDOWN(0.25*0.307,3)))","v":""},""]
[null,null,null,null,"-",null,null,null,null,null,null,"",null,null,"",null,"","",null,{"$f":"IF(OR(AC33=\"\",Q20=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),IF(N20=\"\",\"\",IF(ROUNDUP(AC33/Q20,4) >= MAX(0.25*0.307, 2.5*0.307^(5/4)*N20*K20^0.5/Q20),\"要\",\"不要\")),IF(ROUNDUP(AC33/Q20,4) >= 0.25*0.307,\"要\",\"不要\")))","v":""},null,null,{"$f":"IF(AC33=\"\",\"\",IFERROR(ROUNDUP(IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),MIN(AC33/N20/(0.25*0.307), (AC33/(2.5*0.307^(5/4)*N20))^2),AC33/N20/(0.25*0.307)),2),\"\"))","v":""},"",{"$f":"IF(I20=\"✓\", IFERROR(IF(AC33/Q20 > IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),0.1535,0.307),\"システム見直し必要\",\"\"),\"\"),\"\")","v":""},null,null,null,{"$f":"IF(OR(AC33=\"\",Q20=\"\"),\"\",ROUNDDOWN(AC33/Q20,4))","v":""},null,null,"",{"$f":"IF(OR(K20=\"\",N20=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),ROUNDDOWN(MAX(0.25*0.307, 2.5*0.307^(5/4)*N20*K20^(1/2)/(K20*N20)),3),ROUNDDOWN(0.25*0.307,3)))","v":""},""]
[null,null,null,null,"-",null,null,null,null,null,null,"",null,null,"",null,"","",null,{"$f":"IF(OR(AC33=\"\",Q21=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),IF(N21=\"\",\"\",IF(ROUNDUP(AC33/Q21,4) >= MAX(0.25*0.307, 2.5*0.307^(5/4)*N21*K21^0.5/Q21),\"要\",\"不要\")),IF(ROUNDUP(AC33/Q21,4) >= 0.25*0.307,\"要\",\"不要\")))","v":""},null,null,{"$f":"IF(AC33=\"\",\"\",IFERROR(ROUNDUP(IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),MIN(AC33/N21/(0.25*0.307), (AC33/(2.5*0.307^(5/4)*N21))^2),AC33/N21/(0.25*0.307)),2),\"\"))","v":""},"",{"$f":"IF(I21=\"✓\", IFERROR(IF(AC33/Q21 > IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),0.1535,0.307),\"システム見直し必要\",\"\"),\"\"),\"\")","v":""},null,null,null,{"$f":"IF(OR(AC33=\"\",Q21=\"\"),\"\",ROUNDDOWN(AC33/Q21,4))","v":""},null,null,"",{"$f":"IF(OR(K21=\"\",N21=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),ROUNDDOWN(MAX(0.25*0.307, 2.5*0.307^(5/4)*N21*K21^(1/2)/(K21*N21)),3),ROUNDDOWN(0.25*0.307,3)))","v":""},""]
[null,null,null,null,"-",null,null,null,null,null,null,{"$f":"IF(K22<>\"\",\"㎡\",\"\")","v":""},null,null,{"$f":"IF(N22<>\"\",\"m\",\"\")","v":""},null,{"$f":"IF(OR(K22=\"\", N22=\"\"), \"\", K22*N22)","v":""},{"$f":"IF(Q22<>\"\",\"㎥\",\"\")","v":""},null,{"$f":"IF(OR(AC33=\"\",Q22=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),IF(N22=\"\",\"\",IF(ROUNDUP(AC33/Q22,4) >= MAX(0.25*0.307, 2.5*0.307^(5/4)*N22*K22^0.5/Q22),\"要\",\"不要\")),IF(ROUNDUP(AC33/Q22,4) >= 0.25*0.307,\"要\",\"不要\")))","v":""},null,null,{"$f":"IF(AC33=\"\",\"\",IFERROR(ROUNDUP(IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),MIN(AC33/N22/(0.25*0.307), (AC33/(2.5*0.307^(5/4)*N22))^2),AC33/N22/(0.25*0.307)),2),\"\"))","v":""},{"$f":"IF(W22<>\"\",\"㎡\",\"\")","v":""},{"$f":"IF(I22=\"✓\", IFERROR(IF(AC33/Q22 > IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),0.1535,0.307),\"システム見直し必要\",\"\"),\"\"),\"\")","v":""},null,null,null,{"$f":"IF(OR(AC33=\"\",Q22=\"\"),\"\",ROUNDDOWN(AC33/Q22,4))","v":""},null,null,"",{"$f":"IF(OR(K22=\"\",N22=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),ROUNDDOWN(MAX(0.25*0.307, 2.5*0.307^(5/4)*N22*K22^(1/2)/(K22*N22)),3),ROUNDDOWN(0.25*0.307,3)))","v":""},""]
[null,null,null,null,"-",null,null,null,null,null,null,{"$f":"IF(K23<>\"\",\"㎡\",\"\")","v":""},null,null,{"$f":"IF(N23<>\"\",\"m\",\"\")","v":""},null,{"$f":"IF(OR(K23=\"\", N23=\"\"), \"\", K23*N23)","v":""},{"$f":"IF(Q23<>\"\",\"㎥\",\"\")","v":""},null,{"$f":"IF(OR(AC33=\"\",Q23=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),IF(N23=\"\",\"\",IF(ROUNDUP(AC33/Q23,4) >= MAX(0.25*0.307, 2.5*0.307^(5/4)*N23*K23^0.5/Q23),\"要\",\"不要\")),IF(ROUNDUP(AC33/Q23,4) >= 0.25*0.307,\"要\",\"不要\")))","v":""},null,null,{"$f":"IF(AC33=\"\",\"\",IFERROR(ROUNDUP(IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),MIN(AC33/N23/(0.25*0.307), (AC33/(2.5*0.307^(5/4)*N23))^2),AC33/N23/(0.25*0.307)),2),\"\"))","v":""},{"$f":"IF(W23<>\"\",\"㎡\",\"\")","v":""},{"$f":"IF(I23=\"✓\", IFERROR(IF(AC33/Q23 > IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),0.1535,0.307),\"システム見直し必要\",\"\"),\"\"),\"\")","v":""},null,null,null,{"$f":"IF(OR(AC33=\"\",Q23=\"\"),\"\",ROUNDDOWN(AC33/Q23,4))","v":""},null,null,"",{"$f":"IF(OR(K23=\"\",N23=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),ROUNDDOWN(MAX(0.25*0.307, 2.5*0.307^(5/4)*N23*K23^(1/2)/(K23*N23)),3),ROUNDDOWN(0.25*0.307,3)))","v":""},""]
[null,null,null,null,"-",null,null,null,null,null,null,{"$f":"IF(K24<>\"\",\"㎡\",\"\")","v":""},null,null,{"$f":"IF(N24<>\"\",\"m\",\"\")","v":""},null,{"$f":"IF(OR(K24=\"\", N24=\"\"), \"\", K24*N24)","v":""},{"$f":"IF(Q24<>\"\",\"㎥\",\"\")","v":""},null,{"$f":"IF(OR(AC33=\"\",Q24=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),IF(N24=\"\",\"\",IF(ROUNDUP(AC33/Q24,4) >= MAX(0.25*0.307, 2.5*0.307^(5/4)*N24*K24^0.5/Q24),\"要\",\"不要\")),IF(ROUNDUP(AC33/Q24,4) >= 0.25*0.307,\"要\",\"不要\")))","v":""},null,null,{"$f":"IF(AC33=\"\",\"\",IFERROR(ROUNDUP(IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),MIN(AC33/N24/(0.25*0.307), (AC33/(2.5*0.307^(5/4)*N24))^2),AC33/N24/(0.25*0.307)),2),\"\"))","v":""},{"$f":"IF(W24<>\"\",\"㎡\",\"\")","v":""},{"$f":"IF(I24=\"✓\", IFERROR(IF(AC33/Q24 > IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),0.1535,0.307),\"システム見直し必要\",\"\"),\"\"),\"\")","v":""},null,null,null,{"$f":"IF(OR(AC33=\"\",Q24=\"\"),\"\",ROUNDDOWN(AC33/Q24,4))","v":""},null,null,"",{"$f":"IF(OR(K24=\"\",N24=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),ROUNDDOWN(MAX(0.25*0.307, 2.5*0.307^(5/4)*N24*K24^(1/2)/(K24*N24)),3),ROUNDDOWN(0.25*0.307,3)))","v":""},""]
[null,null,null,null,"-",null,null,null,null,null,null,{"$f":"IF(K25<>\"\",\"㎡\",\"\")","v":""},null,null,{"$f":"IF(N25<>\"\",\"m\",\"\")","v":""},null,{"$f":"IF(OR(K25=\"\", N25=\"\"), \"\", K25*N25)","v":""},{"$f":"IF(Q25<>\"\",\"㎥\",\"\")","v":""},null,{"$f":"IF(OR(AC33=\"\",Q25=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),IF(N25=\"\",\"\",IF(ROUNDUP(AC33/Q25,4) >= MAX(0.25*0.307, 2.5*0.307^(5/4)*N25*K25^0.5/Q25),\"要\",\"不要\")),IF(ROUNDUP(AC33/Q25,4) >= 0.25*0.307,\"要\",\"不要\")))","v":""},null,null,{"$f":"IF(AC33=\"\",\"\",IFERROR(ROUNDUP(IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),MIN(AC33/N25/(0.25*0.307), (AC33/(2.5*0.307^(5/4)*N25))^2),AC33/N25/(0.25*0.307)),2),\"\"))","v":""},{"$f":"IF(W25<>\"\",\"㎡\",\"\")","v":""},{"$f":"IF(I25=\"✓\", IFERROR(IF(AC33/Q25 > IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),0.1535,0.307),\"システム見直し必要\",\"\"),\"\"),\"\")","v":""},null,null,null,{"$f":"IF(OR(AC33=\"\",Q25=\"\"),\"\",ROUNDDOWN(AC33/Q25,4))","v":""},null,null,"",{"$f":"IF(OR(K25=\"\",N25=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),ROUNDDOWN(MAX(0.25*0.307, 2.5*0.307^(5/4)*N25*K25^(1/2)/(K25*N25)),3),ROUNDDOWN(0.25*0.307,3)))","v":""},""]
[null,null,null,null,"-",null,null,null,null,null,null,"",null,null,"",null,"","",null,{"$f":"IF(OR(AC33=\"\",Q26=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),IF(N26=\"\",\"\",IF(ROUNDUP(AC33/Q26,4) >= MAX(0.25*0.307, 2.5*0.307^(5/4)*N26*K26^0.5/Q26),\"要\",\"不要\")),IF(ROUNDUP(AC33/Q26,4) >= 0.25*0.307,\"要\",\"不要\")))","v":""},null,null,{"$f":"IF(AC33=\"\",\"\",IFERROR(ROUNDUP(IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),MIN(AC33/N26/(0.25*0.307), (AC33/(2.5*0.307^(5/4)*N26))^2),AC33/N26/(0.25*0.307)),2),\"\"))","v":""},"",{"$f":"IF(I26=\"✓\", IFERROR(IF(AC33/Q26 > IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),0.1535,0.307),\"システム見直し必要\",\"\"),\"\"),\"\")","v":""},null,null,null,{"$f":"IF(OR(AC33=\"\",Q26=\"\"),\"\",ROUNDDOWN(AC33/Q26,4))","v":""},null,null,"",{"$f":"IF(OR(K26=\"\",N26=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),ROUNDDOWN(MAX(0.25*0.307, 2.5*0.307^(5/4)*N26*K26^(1/2)/(K26*N26)),3),ROUNDDOWN(0.25*0.307,3)))","v":""},""]
[null,null,null,null,"-",null,null,null,null,null,null,{"$f":"IF(K27<>\"\",\"㎡\",\"\")","v":""},null,null,{"$f":"IF(N27<>\"\",\"m\",\"\")","v":""},null,{"$f":"IF(OR(K27=\"\", N27=\"\"), \"\", K27*N27)","v":""},{"$f":"IF(Q27<>\"\",\"㎥\",\"\")","v":""},null,{"$f":"IF(OR(AC33=\"\",Q27=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),IF(N27=\"\",\"\",IF(ROUNDUP(AC33/Q27,4) >= MAX(0.25*0.307, 2.5*0.307^(5/4)*N27*K27^0.5/Q27),\"要\",\"不要\")),IF(ROUNDUP(AC33/Q27,4) >= 0.25*0.307,\"要\",\"不要\")))","v":""},null,null,{"$f":"IF(AC33=\"\",\"\",IFERROR(ROUNDUP(IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),MIN(AC33/N27/(0.25*0.307), (AC33/(2.5*0.307^(5/4)*N27))^2),AC33/N27/(0.25*0.307)),2),\"\"))","v":""},{"$f":"IF(W27<>\"\",\"㎡\",\"\")","v":""},{"$f":"IF(I27=\"✓\", IFERROR(IF(AC33/Q27 > IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),0.1535,0.307),\"システム見直し必要\",\"\"),\"\"),\"\")","v":""},null,null,null,{"$f":"IF(OR(AC33=\"\",Q27=\"\"),\"\",ROUNDDOWN(AC33/Q27,4))","v":""},null,null,"",{"$f":"IF(OR(K27=\"\",N27=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),ROUNDDOWN(MAX(0.25*0.307, 2.5*0.307^(5/4)*N27*K27^(1/2)/(K27*N27)),3),ROUNDDOWN(0.25*0.307,3)))","v":""},""]
[null,null,null,null,"-",null,null,null,null,null,null,"",null,null,"",null,"","",null,{"$f":"IF(OR(AC33=\"\",Q28=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),IF(N28=\"\",\"\",IF(ROUNDUP(AC33/Q28,4) >= MAX(0.25*0.307, 2.5*0.307^(5/4)*N28*K28^0.5/Q28),\"要\",\"不要\")),IF(ROUNDUP(AC33/Q28,4) >= 0.25*0.307,\"要\",\"不要\")))","v":""},null,null,{"$f":"IF(AC33=\"\",\"\",IFERROR(ROUNDUP(IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),MIN(AC33/N28/(0.25*0.307), (AC33/(2.5*0.307^(5/4)*N28))^2),AC33/N28/(0.25*0.307)),2),\"\"))","v":""},"",{"$f":"IF(I28=\"✓\", IFERROR(IF(AC33/Q28 > IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),0.1535,0.307),\"システム見直し必要\",\"\"),\"\"),\"\")","v":""},null,null,null,{"$f":"IF(OR(AC33=\"\",Q28=\"\"),\"\",ROUNDDOWN(AC33/Q28,4))","v":""},null,null,"",{"$f":"IF(OR(K28=\"\",N28=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),ROUNDDOWN(MAX(0.25*0.307, 2.5*0.307^(5/4)*N28*K28^(1/2)/(K28*N28)),3),ROUNDDOWN(0.25*0.307,3)))","v":""},""]
[null,null,null,null,"-",null,null,null,null,null,null,"",null,null,"",null,"","",null,{"$f":"IF(OR(AC33=\"\",Q29=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),IF(N29=\"\",\"\",IF(ROUNDUP(AC33/Q29,4) >= MAX(0.25*0.307, 2.5*0.307^(5/4)*N29*K29^0.5/Q29),\"要\",\"不要\")),IF(ROUNDUP(AC33/Q29,4) >= 0.25*0.307,\"要\",\"不要\")))","v":""},null,null,{"$f":"IF(AC33=\"\",\"\",IFERROR(ROUNDUP(IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),MIN(AC33/N29/(0.25*0.307), (AC33/(2.5*0.307^(5/4)*N29))^2),AC33/N29/(0.25*0.307)),2),\"\"))","v":""},"",{"$f":"IF(I29=\"✓\", IFERROR(IF(AC33/Q29 > IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),0.1535,0.307),\"システム見直し必要\",\"\"),\"\"),\"\")","v":""},null,null,null,{"$f":"IF(OR(AC33=\"\",Q29=\"\"),\"\",ROUNDDOWN(AC33/Q29,4))","v":""},null,null,"",{"$f":"IF(OR(K29=\"\",N29=\"\"),\"\",IF(OR(C14=\"FDC(S)P1121LXZ\",C14=\"FDC(S)P1401LXZ\",C14=\"FDC(S)P1601LXZ\"),ROUNDDOWN(MAX(0.25*0.307, 2.5*0.307^(5/4)*N29*K29^(1/2)/(K29*N29)),3),ROUNDDOWN(0.25*0.307,3)))","v":""},""]
["合計容量","⑥",null,"kW",null,"kg","※室内機合計容量分チャージ量"]
[null,null,null,null,null,null,{"$f":"IF(OR(AND(C14=\"FDC(S)P1121LXZ\",C30<=11.2),AND(C14=\"FDC(S)P1401LXZ\",C30<=14)),\"※室外機容量≧室内機容量のためチャージ不要\",\"\")","v":""},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(C14=\"\", \"\",IF(OR(C14=\"FDC(S)P1121LXZ\", C14=\"FDC(S)P1401LXZ\"),IF(H33+K33+N33+Q33+T33+W33<=20,\"配管長20m以下は追加チャージ不要\",IF(E30+Z34<1,\"追加チャージ不要\",\"\")),\"\"))","v":""}]
[null,null,"冷媒配管サイズ（液管）",null,null,null,null,"φ6.35",null,null,"φ9.52",null,null,"φ12.7",null,null,"φ15.88",null,null,"φ19.05",null,null,"φ22.22",null,"冷媒配管分\nチャージ量合計",null,null,null,"システム冷媒量"]
[null,null,"配管長さ（m）",null,null,null,"⑦",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,"冷媒配管分チャージ量（kg）",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"SUM(N(H34),N(K34),N(N34),N(Q34),N(T34),N(W34))","v":0},"kg",null,null,null,null,"kg"]
[null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(OR(N34=\"-\"), \"主管サイズを超過\", \"\")","v":""},null,null,{"$f":"IF(OR(Q34=\"-\"), \"主管サイズを超過\", \"\")","v":""},null,null,{"$f":"IF(OR(T34=\"-\"), \"主管サイズを超過\", \"\")","v":""},null,null,{"$f":"IF(OR(W34=\"-\"), \"主管サイズを超過\", \"\")","v":""},null,null,{"$f":"IF(C14=\"\", \"\", IF(OR(AND(OR(C14=\"FDC(S)P1121LXZ\", C14=\"FDC(S)P1401LXZ\"), H33+K33+N33+Q33+T33+W33<=20)), \"※配管長20m以下\" & CHAR(10) & \"　 チャージレス\", \"\"))","v":""},null,null,null,{"$f":"IF(OR(AC33<E14), \"冷媒を回収してください\", \"\")","v":""}]

{"sheet":"計算シート","index":1,"n_rows":50,"n_cols":50,"rows_kept":50,"cut":false,"hidden":true,"merged":[[3,20,3,38],[4,12,5,12],[4,1,5,1],[4,7,5,7],[4,5,5,5],[4,6,5,6],[4,2,5,2],[4,3,5,3],[4,13,5,13],[4,49,5,49],[4,14,5,14],[4,17,5,17],[4,47,5,47],[4,40,5,40],[4,15,5,15],[4,16,5,16],[4,44,4,46],[4,20,4,22],[4,23,4,25],[4,35,4,37],[4,42,5,42],[4,29,4,31],[4,32,4,34],[4,41,5,41],[4,39,5,39],[4,0,5,0],[4,4,5,4],[4,48,5,48],[4,19,5,19],[4,8,5,8],[4,9,5,11],[4,38,5,38],[4,18,5,18],[4,26,4,28]]}
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,20]
[null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,20,null,null,null,null,null,null,null,null,2000]
["-",null,"-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,null,"-",null,null,"-",null,null,"-",null,null,"-",null,null,"-",null,"-",null,null,null,"-","E"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"冷媒配管分チャージ量"]
["カタログ\n発行年月","冷媒種","型","標準・ﾘﾌﾚｯｼｭ\n冷暖ﾌﾘｰ・寒冷地","耐重塩害\n仕様","馬力","シリーズ","機種名","室外\n容量","組合せ機種",null,null,"室内機\n接続容量\n(kW)","室内機設置階\n（[地下最下層]\nor[その他]　で選択","出荷時\n充てん量\n(Kg)","部屋面積\nAi（㎡）","漏えい\n想定高さ\nhi（ｍ）","部屋容積\nV（ｍ３）","配管実長\n(m)","主管\nサイズ","φ6.35",null,null,"φ9.52",null,null,"φ12.7",null,null,"φ15.88",null,null,"φ19.05",null,null,"φ22.22",null,null,"冷媒配管分チャージ量\n(kg)","室内機\n合計容量分\nチェージ量\n(kg)","追加チャージ量\n合計\n(Kg)","システム\n冷媒量\n(Kg)","一系統上限値\n(上限がない場合は空欄)","LFL",null,null,null,"判定結果","注意事項\n※一系統封入量上限を超過時メッセージを表示","条件(備考)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"長さ（ｍ）","係数","①\n冷媒量\n(Kg)","長さ（ｍ）","係数","②\n冷媒量\n(Kg)","長さ（ｍ）","係数","③\n冷媒量\n(Kg)","長さ（ｍ）","係数","④\n冷媒量\n(Kg)","長さ（ｍ）","係数","⑤\n冷媒量\n(Kg)","長さ（ｍ）","係数","⑥\n冷媒量\n(Kg)",null,null,null,null,null,"燃焼下限界濃度\n(kg/㎥)","冷媒漏えい時\n最大濃度\n(kg/㎥)","QLMV","ODL"]
[null,"◆１：選択",null,null,null,null,null,"◆２：選択",null,null,null,null,"◆８：Input","◆３：選択",null,"◆４：Input","◆５：Input",null,"◆６：選択",null,"◆７：Input",null,null,"◆７：Input",null,null,"◆７：Input",null,null,"◆７：Input",null,null,"◆７：Input",null,null,"◆７：Input"]
[]
[null,"R32","LXZ","標準",null,4,"サイドフローLXZ","FDC(S)P1121LXZ",11.2,null,null,null,225,null,4.2,null,null,{"$f":"IF(OR(P9=\"\", Q9=\"\"), \"\", P9*Q9)","v":""},"90m未満",{"$f":"IF(S9=\"\",\"\",IF(S9=\"90m未満\",VLOOKUP(B9&D9&\",\"&F9,主管サイズルックアップ用,5,FALSE),VLOOKUP(B9&D9&\",\"&F9,主管サイズルックアップ用,6,FALSE)))","v":9.52},10,0.02,{"$f":"IF($T9=\"***\",\"実長90m超使用不可\",IF($T9<6.35,\"-\",IF(V9=\"***\",\"0\",U9*V9)))","v":0.2},20,0.05,{"$f":"IF($T9=\"***\",\"実長90m超使用不可\",IF($T9<9.52,\"-\",IF(Y9=\"***\",\"0\",X9*Y9)))","v":1},"***","***",{"$f":"IF($T9=\"***\",\"実長90m超使用不可\",IF($T9<12.7,\"-\",IF(AB9=\"***\",\"0\",AA9*AB9)))","v":"-"},"***","***",{"$f":"IF($T9=\"***\",\"実長90m超使用不可\",IF($T9<15.88,\"-\",IF(AE9=\"***\",\"0\",AD9*AE9)))","v":"-"},"***","***",{"$f":"IF($T9=\"***\",\"実長90m超使用不可\",IF($T9<19.05,\"-\",IF(AH9=\"***\",\"0\",AG9*AH9)))","v":"-"},"***","***",{"$f":"IF($T9=\"***\",\"実長90m超使用不可\",IF($T9<22.22,\"-\",IF(AK9=\"***\",\"0\",AJ9*AK9)))","v":"-"},{"$f":"IF(OR(W9=\"実長90m超使用不可\",W9=\"-\"),0,W9)+IF(OR(Z9=\"実長90m超使用不可\",Z9=\"-\"),0,Z9)+IF(OR(AC9=\"実長90m超使用不可\",AC9=\"-\"),0,AC9)+IF(OR(AF9=\"実長90m超使用不可\",AF9=\"-\"),0,AF9)+IF(OR(AI9=\"実長90m超使用不可\",AI9=\"-\"),0,AI9)+IF(OR(AL9=\"実長90m超使用不可\",AL9=\"-\"),0,AL9)","v":1.2},{"$f":"IF(M9 > I9, (M9 - I9) * 0.05, 0)","v":10.690000000000001},{"$f":"IF(AND(U9+X9<=20, U9+X9>=5), 0, IF(AN9+AM9<1, AN9+AM9+3.2-O9, AN9+AM9-1))","v":10.89},{"$f":"O9+AO9","v":15.09},{"$f":"IF(ISERROR(VLOOKUP(C9&D9&\",\"&F9,封入上限ルックアップ用,5,FALSE)),\"\",VLOOKUP(C9&D9&\",\"&F9,封入上限ルックアップ用,5,FALSE))","v":50},7.5999999999999998E-2,{"$f":"IFERROR(IF(R9=0, \"NG\", IF(AP9/R9 <= 0.25*0.307, \"OK\", \"NG\")), \"\")","v":""},{"$f":"IF(B9=\"R410A\",0.42,IF(B9=\"R407C\",0.46,IF(B9=\"R22\",0.28,\"NG\")))","v":"NG"},{"$f":"IF(B9=\"R410A\",0.42,IF(B9=\"R407C\",0.49,IF(B9=\"R22\",0.5,\"NG\")))","v":"NG"},{"$f":"IF(AR9=\"\",\"\",IF(OR(AR9<=AS9,AND(N9=\"その他\",AR9<=AT9)),\"OK\",IF(OR(AND(N9=\"最下層\",AR9<=AT9),AND(N9=\"その他\",AR9<=AU9)),\"対策が１つ必要です\",IF(OR(AND(N9=\"最下層\",AR9<=AU9),AND(N9=\"その他\",AR9>AU9)),\"対策が２つ必要です\",\"システムの見直しが必要です\"))))","v":"OK"},{"$f":"IF(AND(C9=\"LX3\",#REF!>AQ9),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,5,"サイドフローLXZ","FDC(S)P1401LXZ",14,null,null,null,16,"その他",4.2,null,null,{"$f":"IF(OR(P10=\"\", Q10=\"\"), \"\", P10*Q10)","v":""},"90m未満",9.52,28,0.02,{"$f":"IF($T10=\"***\",\"実長90m超使用不可\",IF($T10<6.35,\"-\",IF(V10=\"***\",\"0\",U10*V10)))","v":0.56000000000000005},20,0.05,{"$f":"IF($T10=\"***\",\"実長90m超使用不可\",IF($T10<9.52,\"-\",IF(Y10=\"***\",\"0\",X10*Y10)))","v":1},20,"***",{"$f":"IF($T10=\"***\",\"実長90m超使用不可\",IF($T10<12.7,\"-\",IF(AB10=\"***\",\"0\",AA10*AB10)))","v":"-"},"***","***",{"$f":"IF($T10=\"***\",\"実長90m超使用不可\",IF($T10<15.88,\"-\",IF(AE10=\"***\",\"0\",AD10*AE10)))","v":"-"},"***","***",{"$f":"IF($T10=\"***\",\"実長90m超使用不可\",IF($T10<19.05,\"-\",IF(AH10=\"***\",\"0\",AG10*AH10)))","v":"-"},"***","***",{"$f":"IF($T10=\"***\",\"実長90m超使用不可\",IF($T10<22.22,\"-\",IF(AK10=\"***\",\"0\",AJ10*AK10)))","v":"-"},{"$f":"IF(OR(W10=\"実長90m超使用不可\",W10=\"-\"),0,W10)+IF(OR(Z10=\"実長90m超使用不可\",Z10=\"-\"),0,Z10)+IF(OR(AC10=\"実長90m超使用不可\",AC10=\"-\"),0,AC10)+IF(OR(AF10=\"実長90m超使用不可\",AF10=\"-\"),0,AF10)+IF(OR(AI10=\"実長90m超使用不可\",AI10=\"-\"),0,AI10)+IF(OR(AL10=\"実長90m超使用不可\",AL10=\"-\"),0,AL10)","v":1.56},0.1,{"$f":"IF(AND(U10+X10<=20, U10+X10>=5), 0, IF(AN10+AM10<1, AN10+AM10+3.2-O10, AN10+AM10-1))","v":0.66000000000000014},4.8600000000000003,50,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C10=\"LX3\",#REF!>AQ10),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,6,"サイドフローLXZ","FDC(S)P1601LXZ",16,null,null,null,16,null,2.2000000000000002,null,null,"","90m未満",9.52,20.5,1.9E-2,{"$f":"IF($T11=\"***\",\"実長90m超使用不可\",IF($T11<6.35,\"-\",IF(V11=\"***\",\"0\",U11*V11)))","v":0.38950000000000001},20,5.1999999999999998E-2,1.04,20,"***","-","***","***","-","***","***","-","***","***","-",1.4295,{"$f":"M11*0.075","v":1.2},{"$f":"AM11+AN11","v":2.6295000000000002},4.8295000000000003,50,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C11=\"LX3\",#REF!>AQ11),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZY","標準",null,8,"サイドフローLXZY","FDC(S)P2241LXZY",22.4,null,null,null,22.4,null,6.5,null,null,"","90m以上",12.7,10,1.9E-2,0.19,20,5.1999999999999998E-2,1.04,null,0.1,0,"***","***","-","***","***","-","***","***","-",1.23,{"$f":"M12*0.075","v":1.68},2.91,9.41,50,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C12=\"LX3\",#REF!>AQ12),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZY","標準",null,10,"サイドフローLXZY","FDC(S)P2801LXZY",28,null,null,null,28,"その他",6.5,null,null,"","90m以上",12.7,10,1.9E-2,0.19,10,5.1999999999999998E-2,{"$f":"IF($T13=\"***\",\"実長90m超使用不可\",IF($T13<9.52,\"-\",IF(Y13=\"***\",\"0\",ROUND(X13*Y13,2))))","v":0.52},100,0.1,10,40,"***","-",50,"***","-",50,"***","-",10.71,{"$f":"M13*0.075","v":2.1},12.81,19.310000000000002,50,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C13=\"LX3\",#REF!>AQ13),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,8,"高効率LXZ","FDC(S)P2241LXZ",22.4,null,null,null,20,null,7.7,null,null,"","90m以上",12.7,95,1.9E-2,1.8049999999999999,225,5.1999999999999998E-2,{"$f":"IF($T14=\"***\",\"実長90m超使用不可\",IF($T14<9.52,\"-\",IF(Y14=\"***\",\"0\",X14*Y14)))","v":11.7},null,0.1,0,"***","***","-","***","***","-","***","***","-",13.504999999999999,1.5,15.004999999999999,22.704999999999998,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C14=\"LX3\",#REF!>AQ14),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,10,"高効率LXZ","FDC(S)P2801LXZ",28,null,null,null,14,"その他",7.7,null,null,"","90m以上",12.7,10,1.9E-2,0.19,20,5.1999999999999998E-2,1.04,30,0.1,3,40,"***","-",50,"***","-",50,"***","-",4.2300000000000004,1.05,5.28,12.98,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C15=\"LX3\",#REF!>AQ15),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,12,"高効率LXZ","FDC(S)P3351LXZ",33.5,null,null,null,33.5,null,8.6999999999999993,null,null,"","90m以上",12.7,1,1.9E-2,1.9E-2,20,5.1999999999999998E-2,1.04,30,0.1,3,40,"***","-",50,"***","-","***","***","-",4.0590000000000002,2.5124999999999997,6.5715000000000003,15.2715,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C16=\"LX3\",#REF!>AQ16),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,14,"高効率LXZ","FDC(S)P4001LXZ",40,null,null,null,40,null,8.6999999999999993,null,null,"","90m以上",12.7,20,1.9E-2,0.38,1800,5.1999999999999998E-2,93.6,40,0.1,4,40,"***","-","***","***","-","***","***","-",97.97999999999999,3,100.97999999999999,109.67999999999999,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C17=\"LX3\",#REF!>AQ17),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,16,"高効率LXZ","FDC(S)P4501LXZ",45,null,null,null,45,"その他",8.6999999999999993,null,null,"","90m以上",12.7,10,1.9E-2,0.19,20,5.1999999999999998E-2,1.04,30,0.1,3,40,"***","-",50,"***","-",60,"***","-",4.2300000000000004,3.375,7.6050000000000004,16.305,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C18=\"LX3\",#REF!>AQ18),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,18,"高効率LXZ","FDC(S)P5001LXZ",50,null,null,null,50,null,9.5,null,null,"","90m以上",15.88,20,1.9E-2,0.38,20,5.1999999999999998E-2,1.04,2000,0.1,200,2000,0.16,320,200,"***","-","***","***","-",521.41999999999996,3.75,525.16999999999996,534.66999999999996,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C19=\"LX3\",#REF!>AQ19),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,20,"高効率LXZ","FDC(S)P5601LXZ",56,null,null,null,56,"その他",9.5,null,null,"","90m以上",15.88,100,1.9E-2,1.9,103,5.1999999999999998E-2,5.3559999999999999,100,0.1,10,61,0.16,9.76,"***","***","-","***","***","-",27.015999999999998,4.2,31.215999999999998,40.715999999999994,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C20=\"LX3\",#REF!>AQ20),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,22,"高効率LXZ","FDC(S)P6151LXZ",61.5,"FDCP2801LXZ","FDCP3351LXZ",null,null,null,16.399999999999999,null,null,"","90m以上",15.88,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,"***","***","-","***","***","-",0,0,0,16.399999999999999,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C21=\"LX3\",#REF!>AQ21),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,24,"高効率LXZ","FDC(S)P6701LXZ",67,"FDCP3351LXZ","FDCP3351LXZ",null,null,null,17.399999999999999,null,null,"","90m以上",15.88,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,"***","***","-","***","***","-",0,0,0,17.399999999999999,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C22=\"LX3\",#REF!>AQ22),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,26,"高効率LXZ","FDC(S)P7301LXZ",73,"FDCP3351LXZ","FDCP4001LXZ",null,null,null,17.399999999999999,null,null,"","90m以上",19.05,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,"***","***","-",0,0,0,17.399999999999999,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C23=\"LX3\",#REF!>AQ23),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,28,"高効率LXZ","FDC(S)P7751LXZ",77.5,"FDCP4001LXZ","FDCP4001LXZ",null,null,null,17.399999999999999,null,null,"","90m以上",19.05,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,"***","***","-",0,0,0,17.399999999999999,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C24=\"LX3\",#REF!>AQ24),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,30,"高効率LXZ","FDC(S)P8501LXZ",85,"FDCP4001LXZ","FDCP4501LXZ",null,null,null,17.399999999999999,null,null,"","90m以上",19.05,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,"***","***","-",0,0,0,17.399999999999999,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C25=\"LX3\",#REF!>AQ25),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,32,"高効率LXZ","FDC(S)P9001LXZ",90,"FDCP4501LXZ","FDCP4501LXZ",null,null,null,17.399999999999999,null,null,"","90m以上",19.05,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,"***","***","-",0,0,0,17.399999999999999,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C26=\"LX3\",#REF!>AQ26),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,34,"高効率LXZ","FDC(S)P9501LXZ",95,"FDCP2801LXZ","FDCP3351LXZ","FDCP3351LXZ",null,null,25.1,null,null,"","90m以上",19.05,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,"***","***","-",0,0,0,25.1,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C27=\"LX3\",#REF!>AQ27),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,36,"高効率LXZ","FDC(S)P10001LXZ",100,"FDCP5001LXZ","FDCP5001LXZ",null,null,null,19,null,null,"","90m以上",19.05,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,"***","***","-",0,0,0,19,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C28=\"LX3\",#REF!>AQ28),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,38,"高効率LXZ","FDC(S)P10601LXZ",106,"FDCP5001LXZ","FDCP5601LXZ",null,null,null,19,null,null,"","90m以上",22.22,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,null,0.4,0,0,0,0,19,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C29=\"LX3\",#REF!>AQ29),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,40,"高効率LXZ","FDC(S)P11201LXZ",112,"FDCP5601LXZ","FDCP5601LXZ",null,null,null,19,null,null,"","90m以上",22.22,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,null,0.4,0,0,0,0,19,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C30=\"LX3\",#REF!>AQ30),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,42,"高効率LXZ","FDC(S)P11801LXZ",118,"FDCP4001LXZ","FDCP4001LXZ","FDCP4001LXZ",100,null,26.1,null,null,"","90m以上",22.22,90,1.9E-2,1.71,100,5.1999999999999998E-2,5.2,null,0.1,0,null,0.16,0,null,0.24,0,null,0.4,0,6.91,7.5,14.41,40.510000000000005,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C31=\"LX3\",#REF!>AQ31),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,40,"高効率LXZ","FDC(S)P12201LXZ",122,"FDCP4001LXZ","FDCP4001LXZ","FDCP4501LXZ",122,null,26.1,null,null,"","90m以上",22.22,20,1.9E-2,0.38,20,5.1999999999999998E-2,1.04,30,0.1,3,40,0.16,6.4,50,0.24,12,60,0.4,24,46.82,9.15,55.97,82.07,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C32=\"LX3\",#REF!>AQ32),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,46,"高効率LXZ","FDC(S)P12801LXZ",128,"FDCP4001LXZ","FDCP4501LXZ","FDCP4501LXZ",null,null,26.1,null,null,"","90m以上",22.22,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,null,0.4,0,0,0,0,26.1,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C33=\"LX3\",#REF!>AQ33),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,48,"高効率LXZ","FDC(S)P13601LXZ",136,"FDCP4501LXZ","FDCP4501LXZ","FDCP4501LXZ",null,null,26.1,null,null,"","90m以上",22.22,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,null,0.4,0,0,0,0,26.1,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C34=\"LX3\",#REF!>AQ34),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,54,"高効率LXZ","FDC(S)P15001LXZ",150,"FDCP5001LXZ","FDCP5001LXZ","FDCP5001LXZ",null,null,28.5,null,null,"","90m以上",22.22,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,null,0.4,0,0,0,0,28.5,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C35=\"LX3\",#REF!>AQ35),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,12,"省スペースLXZ","FDC(S)P3351LXZ-N",33.5,null,null,null,null,null,7.7,null,null,"","90m以上",12.7,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,"***","***","-","***","***","-","***","***","-",0,0,0,7.7,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C36=\"LX3\",#REF!>AQ36),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,18,"省スペースLXZ","FDC(S)P5001LXZ-N",50,null,null,null,null,null,8.6999999999999993,null,null,"","90m以上",15.88,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,"***","***","-","***","***","-",0,0,0,8.6999999999999993,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C37=\"LX3\",#REF!>AQ37),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,22,"省スペースLXZ","FDC(S)P6151LXZ-N",61.5,null,null,null,null,null,9.5,null,null,"","90m以上",15.88,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,"***","***","-","***","***","-",0,0,0,9.5,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C38=\"LX3\",#REF!>AQ38),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,24,"省スペースLXZ","FDC(S)P6701LXZ-N",67,null,null,null,null,null,9.5,null,null,"","90m以上",15.88,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,"***","***","-","***","***","-",0,0,0,9.5,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C39=\"LX3\",#REF!>AQ39),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,26,"省スペースLXZ","FDC(S)P7301LXZ-D",73,"FDCP3351LXZ-N","FDCP4001LXZ",null,73,null,16.399999999999999,null,null,"","90m以上",19.05,50,1.9E-2,0.95,50,5.1999999999999998E-2,2.6,50,0.1,5,30,0.16,4.8,50,0.24,12,50,"***","-",25.35,5.4749999999999996,30.825000000000003,47.225000000000001,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C40=\"LX3\",#REF!>AQ40),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,34,"省スペースLXZ","FDC(S)P9501LXZ-D",95,"FDCP4501LXZ","FDCP5001LXZ-N",null,null,null,17.399999999999999,null,null,"","90m以上",19.05,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,"***","***","-",0,0,0,17.399999999999999,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C41=\"LX3\",#REF!>AQ41),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,36,"省スペースLXZ","FDC(S)P10001LXZ-D",100,"FDCP5001LXZ-N","FDCP5001LXZ-N",null,100,null,17.399999999999999,null,null,"","90m以上",19.05,20,1.9E-2,0.38,30,5.1999999999999998E-2,1.5599999999999998,40,0.1,4,50,0.16,8,60,0.24,14.399999999999999,70,"***","-",28.339999999999996,7.5,35.839999999999996,53.239999999999995,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C42=\"LX3\",#REF!>AQ42),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,38,"省スペースLXZ","FDC(S)P10601LXZ-T",106,"FDCP3351LXZ-N","FDCP3351LXZ-N","FDCP4001LXZ",null,null,24.1,null,null,"","90m以上",22.22,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,null,0.4,0,0,0,0,24.1,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C43=\"LX3\",#REF!>AQ43),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,42,"省スペースLXZ","FDC(S)P11801LXZ-D",118,"FDCP5601LXZ","FDCP6151LXZ-N",null,null,null,19,null,null,{"$f":"IF(OR(P44=\"\", Q44=\"\"), \"\", P44*Q44)","v":""},"90m以上",22.22,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,null,0.4,0,0,0,0,19,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C44=\"LX3\",#REF!>AQ44),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,44,"省スペースLXZ","FDC(S)P12201LXZ-D",122,"FDCP6151LXZ-N","FDCP6151LXZ-N",null,null,null,19,null,null,"","90m以上",22.22,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,null,0.4,0,0,0,0,19,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C45=\"LX3\",#REF!>AQ45),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,46,"省スペースLXZ","FDC(S)P12801LXZ-D",128,"FDCP6151LXZ-N","FDCP6701LXZ-N",null,null,null,19,null,null,"","90m以上",22.22,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,null,0.4,0,0,0,0,19,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C46=\"LX3\",#REF!>AQ46),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,48,"省スペースLXZ","FDC(S)P13601LXZ-D",136,"FDCP6701LXZ-N","FDCP6701LXZ-N",null,null,null,19,null,null,"","90m以上",22.22,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,null,0.4,0,0,0,0,19,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C47=\"LX3\",#REF!>AQ47),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,50,"省スペースLXZ","FDC(S)P14001LXZ-T",140,"FDCP4501LXZ","FDCP4501LXZ","FDCP5001LXZ-N",null,null,26.1,null,null,"","90m以上",22.22,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,null,0.4,0,0,0,0,26.1,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C48=\"LX3\",#REF!>AQ48),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,52,"省スペースLXZ","FDC(S)P14501LXZ-T",145,"FDCP4501LXZ","FDCP5001LXZ-N","FDCP5001LXZ-N",null,null,26.1,null,null,"","90m以上",22.22,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,null,0.4,0,0,0,0,26.1,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C49=\"LX3\",#REF!>AQ49),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]
[null,"R32","LXZ","標準",null,54,"省スペースLXZ","FDC(S)P15001LXZ-T",150,"FDCP5001LXZ-N","FDCP5001LXZ-N","FDCP5001LXZ-N",null,null,26.1,null,null,"","90m以上",22.22,null,1.9E-2,0,null,5.1999999999999998E-2,0,null,0.1,0,null,0.16,0,null,0.24,0,null,0.4,0,0,0,0,26.1,63.8,7.5999999999999998E-2,"","NG","NG","OK",{"$f":"IF(AND(C50=\"LX3\",#REF!>AQ50),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#REF!"}}]

{"sheet":"取説","index":2,"n_rows":889,"n_cols":55,"rows_kept":889,"cut":false,"hidden":true,"merged":[[2,0,3,0],[2,1,3,1],[2,2,3,2],[2,3,3,3],[2,4,3,4],[2,5,3,5],[2,6,3,6],[2,7,3,7],[2,8,3,8],[2,9,3,12],[2,13,3,13],[2,14,3,14],[2,15,3,15],[2,16,3,16],[2,17,3,17],[2,18,2,20],[2,21,2,23],[2,24,2,26],[2,27,2,29],[2,30,2,32],[2,33,2,35],[2,36,2,38],[2,39,3,39],[2,40,3,40],[2,52,3,52],[2,53,3,53],[2,54,3,54],[2,41,3,41],[2,42,3,42],[2,43,3,43],[2,44,3,44],[2,46,3,46],[2,49,2,51]]}
[null,"【取説】冷媒量算出ツール"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"B","A",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"C",null,"D","E"]
["カタログ\n発行年月","冷媒種","型","寒冷地","冷暖フリー","容量","シリーズ","機種名","仕区","組合せ機種",null,null,null,"室内機設置階\n（地下の　[最下層]\nor[その他]　で選択","出荷時\n充てん量","室内容積\n（ｍ３）","配管実長\n(m)","主管\nサイズ","φ6.35",null,null,"φ9.52",null,null,"φ12.7",null,null,"φ15.88",null,null,"φ19.05",null,null,"φ22.22",null,null,"φ25.4",null,null,"①～⑦\n単純\n合計","冷暖フリーは\n*1.2,1.3,1.4","①～⑦\n合計\n(Kg)","室内機\n接続容量\n(kW)","係数","⑧\n冷媒量","現地","一系統\n上限値","システム","D/A","限界濃度",null,null,"判定","注意事項\n※一系統封入量上限を超過時メッセージを表示","条件(備考)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"長さ（ｍ）","係数","①\n冷媒量\n(Kg)","長さ（ｍ）","係数","②\n冷媒量\n(Kg)","長さ（ｍ）","係数","③\n冷媒量\n(Kg)","長さ（ｍ）","係数","④\n冷媒量\n(Kg)","長さ（ｍ）","係数","⑤\n冷媒量\n(Kg)","長さ（ｍ）","係数","⑥\n冷媒量\n(Kg)","長さ（ｍ）","係数","⑦\n冷媒量\n(Kg)",null,null,null,null,null,null,"①～⑧",null,"充てん量\n(B+C)","冷媒濃度","RCL","QLMV","ODL"]
[null,"①選択",null,null,null,null,null,"②選択",null,null,null,null,null,"③選択",null,"④入力","⑤選択",null,"⑥入力",null,null,"⑥入力",null,null,"⑥入力",null,null,"⑥入力",null,null,"⑥入力",null,null,"⑥入力",null,null,"⑥入力",null,null,null,null,null,"⑦"]
[]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HKXI2    "," ","ISU13KX2","FDCJ280HKXI2    ",null,null,"その他",11,null,null,{"$f":"IF(Q7=\"\",\"\",IF(Q7=\"90m未満\",VLOOKUP(C7&D7&\",\"&F7,主管サイズルックアップ用,5,FALSE),VLOOKUP(C7&D7&\",\"&F7,主管サイズルックアップ用,6,FALSE)))","v":""},null,0.03,{"$f":"IF($R7=\"***\",\"実長90m超使用不可\",IF($R7<6.35,\"-主管サイズを超過-\",IF(T7=\"***\",\"0\",S7*T7)))","v":0},null,0.06,{"$f":"IF($R7=\"***\",\"実長90m超使用不可\",IF($R7<9.52,\"-主管サイズを超過-\",IF(W7=\"***\",\"0\",V7*W7)))","v":0},null,0.12,{"$f":"IF($R7=\"***\",\"実長90m超使用不可\",IF($R7<12.7,\"-主管サイズを超過-\",IF(Z7=\"***\",\"0\",Y7*Z7)))","v":0},null,"***",{"$f":"IF($R7=\"***\",\"実長90m超使用不可\",IF($R7<15.88,\"-主管サイズを超過-\",IF(AC7=\"***\",\"0\",AB7*AC7)))","v":"0"},null,"***",{"$f":"IF($R7=\"***\",\"実長90m超使用不可\",IF($R7<19.05,\"-主管サイズを超過-\",IF(AF7=\"***\",\"0\",AE7*AF7)))","v":"0"},null,"***",{"$f":"IF($R7=\"***\",\"実長90m超使用不可\",IF($R7<22.22,\"-主管サイズを超過-\",IF(AI7=\"***\",\"0\",AH7*AI7)))","v":"0"},null,"***",{"$f":"IF($R7=\"***\",\"実長90m超使用不可\",IF($R7<25.4,\"-主管サイズを超過-\",IF(AL7=\"***\",\"0\",AK7*AL7)))","v":"0"},{"$f":"IF(OR(U7=\"実長90m超使用不可\",U7=\"-主管サイズを超過-\"),0,U7)+IF(OR(X7=\"実長90m超使用不可\",X7=\"-主管サイズを超過-\"),0,X7)+IF(OR(AA7=\"実長90m超使用不可\",AA7=\"-主管サイズを超過-\"),0,AA7)+IF(OR(AD7=\"実長90m超使用不可\",AD7=\"-主管サイズを超過-\"),0,AD7)+IF(OR(AG7=\"実長90m超使用不可\",AG7=\"-主管サイズを超過-\"),0,AG7)+IF(OR(AJ7=\"実長90m超使用不可\",AJ7=\"-主管サイズを超過-\"),0,AJ7)+IF(OR(AM7=\"実長90m超使用不可\",AM7=\"-主管サイズを超過-\"),0,AM7)","v":0},null,{"$f":"AN7*AO7","v":0},null,17.399999999999999,{"$f":"AR7","v":17.399999999999999},{"$f":"IF(AP7+AS7<0,0,AP7+AS7)","v":17.399999999999999},{"$f":"VLOOKUP(C7&D7&\",\"&F7,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},{"$f":"O7+AT7","v":28.4},{"$f":"IF(ISERROR(AV7/P7),\"\",AV7/P7)","v":""},{"$f":"IF(B7=\"R410A\",0.39,IF(B7=\"R407C\",0.27,IF(B7=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B7=\"R410A\",0.42,IF(B7=\"R407C\",0.46,IF(B7=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(B7=\"R410A\",0.42,IF(B7=\"R407C\",0.49,IF(B7=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(AW7=\"\",\"\",IF(OR(AW7<=AX7,AND(N7=\"その他\",AW7<=AY7)),\"OK\",IF(OR(AND(N7=\"最下層\",AW7<=AY7),AND(N7=\"その他\",AW7<=AZ7)),\"対策が１つ必要です\",IF(OR(AND(N7=\"最下層\",AW7<=AZ7),AND(N7=\"その他\",AW7>AZ7)),\"対策が２つ必要です\",\"システムの見直しが必要です\"))))","v":""}]
[null,"R22","未分類",null,null,355,"FDCJ","FDCJ355HKXI2    "," ","ISU16KX2","FDCJ355HKXI2    ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,{"$f":"AN8*AO8","v":0},null,{"$f":"IF(AQ8<=8,12,IF(AQ8<=13,12+(ROUNDDOWN(AQ8,0)-8)*0.5,\"台数ｵｰﾊﾞ\"))","v":12},12,12,{"$error":"#N/A"},32,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCSJ","FDCSJ280HKXI2   "," ","ISU13KX2","FDCSJ280HKXI2   ",null,null,"その他",11,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,17.399999999999999,17.399999999999999,17.399999999999999,{"$error":"#N/A"},28.4,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,355,"FDCSJ","FDCSJ355HKXI2   "," ","ISU16KX2","FDCSJ355HKXI2   ",null,null,"最下層",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,{"$f":"IF(AQ10<=8,12,IF(AQ10<=13,12+(ROUNDDOWN(AQ10,0)-8)*0.5,\"台数ｵｰﾊﾞ\"))","v":12},12,12,{"$error":"#N/A"},32,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,140,"FDCJ","FDCJ140HKX2A    "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,160,"FDCJ","FDCJ160HKX2A    "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCJ","FDCJ224HKX2A    "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HKX2A    "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,355,"FDCJ","FDCJ355HKXA     "," ",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,{"$f":"IF(AQ15<=8,0,IF(AQ15<=13,(ROUNDDOWN(AQ15,0)-8)*0.5,\"台数ｵｰﾊﾞ\"))","v":0},0,0,{"$error":"#N/A"},20,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,450,"FDCJ","FDCJ450HKXA     "," ",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,{"$f":"IF(AQ16<=8,0,IF(AQ16<=16,(ROUNDDOWN(AQ16,0)-8)*0.5,\"台数ｵｰﾊﾞ\"))","v":0},0,0,{"$error":"#N/A"},20,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCJ","FDCJ224HKX2A-K  "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HKX2A-K  "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,224,"FDCJ","FDCJ224HKX2A-KT "," ",null,null,null,null,"その他",5,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},5,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HKX2A-KT "," ",null,null,null,null,"その他",7,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},7,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ225HKX2A-KT "," ",null,null,null,null,"その他",5,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},5,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ281HKX2A-KT "," ",null,null,null,null,"その他",7,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},7,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ500HKX2A",null,"FDCJ280HKX2A-K  ","FDCJ224HKX2A-KT ",null,null,"その他",{"$f":"12+5","v":17},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,560,"FDCJ","FDCJ560HKX2A",null,"FDCJ280HKX2A-K  ","FDCJ280HKX2A-KT ",null,null,"その他",{"$f":"12+7","v":19},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ672HKX2A",null,"FDCJ224HKX2A-K  ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ728HKX2A",null,"FDCJ280HKX2A-K  ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ784HKX2A",null,"FDCJ280HKX2A-K  ","FDCJ224HKX2A-KT ","FDCJ280HKX2A-KT ",null,"その他",{"$f":"12+5+7","v":24},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},24,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ840HKX2A",null,"FDCJ280HKX2A-K  ","FDCJ280HKX2A-KT ","FDCJ280HKX2A-KT ",null,"その他",{"$f":"12+7+7","v":26},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},26,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ500HKX2AF",null,"FDCJ280HKX2A-K  ","FDCJ225HKX2A-KT ",null,null,"その他",{"$f":"12+5","v":17},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,560,"FDCJ","FDCJ560HKX2AF",null,"FDCJ280HKX2A-K  ","FDCJ281HKX2A-KT ",null,null,"その他",{"$f":"12+7","v":19},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,{"$f":"AR30","v":0},0,{"$error":"#N/A"},19,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ672HKX2AF",null,"FDCJ224HKX2A-K  ","FDCJ225HKX2A-KT ","FDCJ225HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ728HKX2AF",null,"FDCJ280HKX2A-K  ","FDCJ225HKX2A-KT ","FDCJ224HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ784HKX2AF",null,"FDCJ280HKX2A-K  ","FDCJ225HKX2A-KT ","FDCJ281HKX2A-KT ",null,"その他",{"$f":"12+5+7","v":24},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},24,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ840HKX2AF",null,"FDCJ280HKX2A-K  ","FDCJ281HKX2A-KT ","FDCJ281HKX2A-KT ",null,"その他",{"$f":"12+7+7","v":26},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},26,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCSJ","FDCSJ224HKX2A-K "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,280,"FDCSJ","FDCSJ280HKX2A-K "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,224,"FDCSJ","FDCSJ224HKX2A-KT"," ",null,null,null,null,"その他",5,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},5,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,280,"FDCSJ","FDCSJ280HKX2A-KT"," ",null,null,null,null,"その他",7,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},7,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ225HKX2A-KT"," ",null,null,null,null,"その他",5,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},5,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ281HKX2A-KT"," ",null,null,null,null,"その他",7,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},7,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ500HKX2A",null,"FDCSJ280HKX2A-K  ","FDCSJ224HKX2A-KT ",null,null,"その他",{"$f":"12+5","v":17},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,560,"FDCSJ","FDCSJ560HKX2A",null,"FDCSJ280HKX2A-K  ","FDCSJ280HKX2A-KT ",null,null,"その他",{"$f":"12+7","v":19},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ672HKX2A",null,"FDCSJ224HKX2A-K  ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ728HKX2A",null,"FDCSJ280HKX2A-K  ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ784HKX2A",null,"FDCSJ280HKX2A-K  ","FDCSJ224HKX2A-KT ","FDCSJ280HKX2A-KT ",null,"その他",{"$f":"12+5+7","v":24},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},24,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ840HKX2A",null,"FDCSJ280HKX2A-K  ","FDCSJ280HKX2A-KT ","FDCSJ280HKX2A-KT ",null,"その他",{"$f":"12+7+7","v":26},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},26,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ500HKX2AF",null,"FDCSJ280HKX2A-K  ","FDCSJ225HKX2A-KT ",null,null,"その他",{"$f":"12+5","v":17},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,560,"FDCSJ","FDCSJ560HKX2AF",null,"FDCSJ280HKX2A-K  ","FDCSJ281HKX2A-KT ",null,null,"その他",{"$f":"12+7","v":19},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ672HKX2AF",null,"FDCSJ224HKX2A-K  ","FDCSJ225HKX2A-KT ","FDCSJ225HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ728HKX2AF",null,"FDCSJ280HKX2A-K  ","FDCSJ225HKX2A-KT ","FDCSJ224HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ784HKX2AF",null,"FDCSJ280HKX2A-K  ","FDCSJ225HKX2A-KT ","FDCSJ281HKX2A-KT ",null,"その他",{"$f":"12+5+7","v":24},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},24,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ840HKX2AF",null,"FDCSJ280HKX2A-K  ","FDCSJ281HKX2A-KT ","FDCSJ281HKX2A-KT ",null,"その他",{"$f":"12+7+7","v":26},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},26,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCJ","FDCJ224HKXRA    "," ",null,null,null,null,"その他",11,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HKXRA    "," ",null,null,null,null,"その他",11,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,560,"FDCJ","FDCJ560HKXRA    "," ",null,null,null,null,"その他",29,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},29,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCSJ","FDCSJ224HKXRA   "," ",null,null,null,null,"その他",11,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCSJ","FDCSJ280HKXRA   "," ",null,null,null,null,"その他",11,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,560,"FDCSJ","FDCSJ560HKXRA   "," ",null,null,null,null,"その他",29,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},29,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCJ","FDCJ224HKXRWA   "," ",null,null,null,null,"その他",11,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HKXRWA   "," ",null,null,null,null,"その他",11,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCJ","FDCJ224HMXA     "," ",null,null,null,null,"その他",11,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HMXA     "," ",null,null,null,null,"その他",11.4,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11.4,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCSJ","FDCSJ224HMXA    "," ",null,null,null,null,"その他",11,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCSJ","FDCSJ280HMXA    "," ",null,null,null,null,"その他",11.4,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11.4,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCJ","FDCJ224HMXA-K   "," ",null,null,null,null,"その他",11,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HMXA-K   "," ",null,null,null,null,"その他",11.4,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11.4,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCSJ","FDCSJ224HMXA-K  "," ",null,null,null,null,"その他",11,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCSJ","FDCSJ280HMXA-K  "," ",null,null,null,null,"その他",11.4,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11.4,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,450,"FDCJ","FDCJ450HMXA"," ","FDCJ224HMXA-K   ","FDCJ224HMXA-K   ",null,null,"その他",{"$f":"11+11","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ500HMXA"," ","FDCJ224HMXA-K   ","FDCJ280HMXA-K   ",null,null,"その他",{"$f":"11+11.4","v":22.4},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},22.4,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,560,"FDCJ","FDCJ560HMXA"," ","FDCJ280HMXA-K   ","FDCJ280HMXA-K   ",null,null,"その他",{"$f":"11.4+11.4","v":22.8},null,null,{"$f":"IF(Q71=\"\",\"\",IF(Q71=\"90m未満\",VLOOKUP(C71&D71&\",\"&F71,主管サイズルックアップ用,5,FALSE),VLOOKUP(C71&D71&\",\"&F71,主管サイズルックアップ用,6,FALSE)))","v":""},null,0.03,{"$f":"IF($R71=\"***\",\"実長90m超使用不可\",IF($R71<6.35,\"-主管サイズを超過-\",IF(T71=\"***\",\"0\",S71*T71)))","v":0},null,0.06,{"$f":"IF($R71=\"***\",\"実長90m超使用不可\",IF($R71<9.52,\"-主管サイズを超過-\",IF(W71=\"***\",\"0\",V71*W71)))","v":0},null,0.12,{"$f":"IF($R71=\"***\",\"実長90m超使用不可\",IF($R71<12.7,\"-主管サイズを超過-\",IF(Z71=\"***\",\"0\",Y71*Z71)))","v":0},null,0.2,{"$f":"IF($R71=\"***\",\"実長90m超使用不可\",IF($R71<15.88,\"-主管サイズを超過-\",IF(AC71=\"***\",\"0\",AB71*AC71)))","v":0},null,0.28000000000000003,{"$f":"IF($R71=\"***\",\"実長90m超使用不可\",IF($R71<19.05,\"-主管サイズを超過-\",IF(AF71=\"***\",\"0\",AE71*AF71)))","v":0},null,0.4,{"$f":"IF($R71=\"***\",\"実長90m超使用不可\",IF($R71<22.22,\"-主管サイズを超過-\",IF(AI71=\"***\",\"0\",AH71*AI71)))","v":0},null,"***",{"$f":"IF($R71=\"***\",\"実長90m超使用不可\",IF($R71<25.4,\"-主管サイズを超過-\",IF(AL71=\"***\",\"0\",AK71*AL71)))","v":"0"},{"$f":"IF(OR(U71=\"実長90m超使用不可\",U71=\"-主管サイズを超過-\"),0,U71)+IF(OR(X71=\"実長90m超使用不可\",X71=\"-主管サイズを超過-\"),0,X71)+IF(OR(AA71=\"実長90m超使用不可\",AA71=\"-主管サイズを超過-\"),0,AA71)+IF(OR(AD71=\"実長90m超使用不可\",AD71=\"-主管サイズを超過-\"),0,AD71)+IF(OR(AG71=\"実長90m超使用不可\",AG71=\"-主管サイズを超過-\"),0,AG71)+IF(OR(AJ71=\"実長90m超使用不可\",AJ71=\"-主管サイズを超過-\"),0,AJ71)+IF(OR(AM71=\"実長90m超使用不可\",AM71=\"-主管サイズを超過-\"),0,AM71)","v":0},null,0,null,0,{"$f":"AR71","v":0},{"$f":"IF(AP71+AS71<0,0,AP71+AS71)","v":0},{"$f":"VLOOKUP(C71&D71&\",\"&F71,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},{"$f":"O71+AT71","v":22.8},{"$f":"IF(ISERROR(AV71/P71),\"\",AV71/P71)","v":""},{"$f":"IF(B71=\"R410A\",0.39,IF(B71=\"R407C\",0.27,IF(B71=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B71=\"R410A\",0.42,IF(B71=\"R407C\",0.46,IF(B71=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(B71=\"R410A\",0.42,IF(B71=\"R407C\",0.49,IF(B71=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(AW71=\"\",\"\",IF(OR(AW71<=AX71,AND(N71=\"その他\",AW71<=AY71)),\"OK\",IF(OR(AND(N71=\"最下層\",AW71<=AY71),AND(N71=\"その他\",AW71<=AZ71)),\"対策が１つ必要です\",IF(OR(AND(N71=\"最下層\",AW71<=AZ71),AND(N71=\"その他\",AW71>AZ71)),\"対策が２つ必要です\",\"システムの見直しが必要です\"))))","v":""}]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ672HMXA"," ","FDCJ224HMXA-K   ","FDCJ224HMXA-K   ","FDCJ224HMXA-K   ",null,"その他",{"$f":"11+11+11","v":33},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,{"$f":"AN72*AO72","v":0},null,0,0,0,{"$error":"#N/A"},33,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ728HMXA"," ","FDCJ224HMXA-K   ","FDCJ224HMXA-K   ","FDCJ280HMXA-K   ",null,"その他",{"$f":"11+11+11.4","v":33.4},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},33.4,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ784HMXA"," ","FDCJ224HMXA-K   ","FDCJ280HMXA-K   ","FDCJ280HMXA-K   ",null,"その他",{"$f":"11+11.4+11.4","v":33.799999999999997},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},33.799999999999997,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ840HMXA"," ","FDCJ280HMXA-K   ","FDCJ280HMXA-K   ","FDCJ280HMXA-K   ",null,"その他",{"$f":"11.4+11.4+11.4","v":34.200000000000003},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34.200000000000003,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,450,"FDCSJ","FDCSJ450HMXA"," ","FDCSJ224HMXA-K  ","FDCSJ224HMXA-K  ",null,null,"その他",{"$f":"11+11","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ500HMXA"," ","FDCSJ224HMXA-K  ","FDCSJ280HMXA-K  ",null,null,"その他",{"$f":"11+11.4","v":22.4},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},22.4,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,560,"FDCSJ","FDCSJ560HMXA"," ","FDCSJ280HMXA-K  ","FDCSJ280HMXA-K  ",null,null,"その他",{"$f":"11.4+11.4","v":22.8},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},22.8,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ672HMXA"," ","FDCSJ224HMXA-K  ","FDCSJ224HMXA-K  ","FDCSJ224HMXA-K  ",null,"その他",{"$f":"11+11+11","v":33},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},33,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ728HMXA"," ","FDCSJ224HMXA-K  ","FDCSJ224HMXA-K  ","FDCSJ280HMXA-K  ",null,"その他",{"$f":"11+11+11.4","v":33.4},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},33.4,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ784HMXA"," ","FDCSJ224HMXA-K  ","FDCSJ280HMXA-K  ","FDCSJ280HMXA-K  ",null,"その他",{"$f":"11+11.4+11.4","v":33.799999999999997},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},33.799999999999997,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ840HMXA"," ","FDCSJ280HMXA-K  ","FDCSJ280HMXA-K  ","FDCSJ280HMXA-K  ",null,"その他",{"$f":"11.4+11.4+11.4","v":34.200000000000003},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34.200000000000003,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,112,"FDCJ","FDCJ112HSXA     "," ",null,null,null,null,"その他",3.5,null,null,"",null,0.03,0,null,0.06,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},3.5,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,140,"FDCJ","FDCJ140HSXA     "," ",null,null,null,null,"その他",3.5,null,null,"",null,0.03,0,null,0.06,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},3.5,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,160,"FDCJ","FDCJ160HSXA     "," ",null,null,null,null,"その他",3.5,null,null,"",null,0.03,0,null,0.06,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},3.5,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,112,"FDCSJ","FDCSJ112HSXA    "," ",null,null,null,null,"その他",3.5,null,null,"",null,0.03,0,null,0.06,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},3.5,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,140,"FDCSJ","FDCSJ140HSXA    "," ",null,null,null,null,"その他",3.5,null,null,"",null,0.03,0,null,0.06,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},3.5,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,160,"FDCSJ","FDCSJ160HSXA    "," ",null,null,null,null,"その他",3.5,null,null,"",null,0.03,0,null,0.06,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},3.5,"",0.21,0.28000000000000003,0.5,""]
[null,"R407C","未分類",null,null,140,"FDCP","FDCP140HKX2A    "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,160,"FDCP","FDCP160HKX2A    "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,224,"FDCP","FDCP224HKX2A    "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCP","FDCP280HKX2A    "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,""]
[null,"R22","未分類",null,null,140,"FDCSJ","FDCSJ140HKX2A   "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,160,"FDCSJ","FDCSJ160HKX2A   "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCSJ","FDCSJ224HKX2A   "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCSJ","FDCSJ280HKX2A   "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,355,"FDCSJ","FDCSJ355HKX2A   "," ",null,null,null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},16.350000000000001,"",{"$f":"IF(B97=\"R410A\",0.39,IF(B97=\"R407C\",0.27,IF(B97=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B97=\"R410A\",0.42,IF(B97=\"R407C\",0.46,IF(B97=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,""]
[null,"R22","未分類",null,null,450,"FDCSJ","FDCSJ450HKX2A   "," ",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},20,"",{"$f":"IF(B98=\"R410A\",0.39,IF(B98=\"R407C\",0.27,IF(B98=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B98=\"R410A\",0.42,IF(B98=\"R407C\",0.46,IF(B98=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,""]
[null,"R22","未分類",null,null,355,"FDCSJ","FDCSJ355HKXA    "," ",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,{"$f":"IF(AQ99<=8,0,IF(AQ99<=13,(ROUNDDOWN(AQ99,0)-8)*0.5,\"台数ｵｰﾊﾞ\"))","v":0},0,0,{"$error":"#N/A"},20,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,450,"FDCSJ","FDCSJ450HKXA    "," ",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,{"$f":"IF(AQ100<=8,0,IF(AQ100<=16,(ROUNDDOWN(AQ100,0)-8)*0.5,\"台数ｵｰﾊﾞ\"))","v":0},0,0,{"$error":"#N/A"},20,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,560,"FDCSJ","FDCSJ560HKXA    "," ",null,null,null,null,"その他",26,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,{"$f":"IF(AQ101<=8,0,IF(AQ101<=16,(ROUNDDOWN(AQ101,0)-8)*0.5,\"台数ｵｰﾊﾞ\"))","v":0},0,0,{"$error":"#N/A"},26,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ672HKXA    "," ",null,null,null,null,"その他",26,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},26,"",{"$f":"IF(B102=\"R410A\",0.39,IF(B102=\"R407C\",0.27,IF(B102=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B102=\"R410A\",0.42,IF(B102=\"R407C\",0.46,IF(B102=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ728HKXA    "," ",null,null,null,null,"その他",40,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},40,"",{"$f":"IF(B103=\"R410A\",0.39,IF(B103=\"R407C\",0.27,IF(B103=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B103=\"R410A\",0.42,IF(B103=\"R407C\",0.46,IF(B103=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ784HKXA    "," ",null,null,null,null,"その他",40,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},40,"",{"$f":"IF(B104=\"R410A\",0.39,IF(B104=\"R407C\",0.27,IF(B104=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B104=\"R410A\",0.42,IF(B104=\"R407C\",0.46,IF(B104=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ840HKXA    "," ",null,null,null,null,"その他",40,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},40,"",{"$f":"IF(B105=\"R410A\",0.39,IF(B105=\"R407C\",0.27,IF(B105=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B105=\"R410A\",0.42,IF(B105=\"R407C\",0.46,IF(B105=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,""]
[null,"R22","未分類",null,null,560,"FDCJ","FDCJ560HKXA     "," ",null,null,null,null,"その他",26,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,{"$f":"IF(AQ106<=8,0,IF(AQ106<=16,(ROUNDDOWN(AQ106,0)-8)*0.5,\"台数ｵｰﾊﾞ\"))","v":0},0,0,{"$error":"#N/A"},26,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ672HKXA     "," ",null,null,null,null,"その他",26,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},26,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ728HKXA     "," ",null,null,null,null,"その他",40,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},40,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ784HKXA     "," ",null,null,null,null,"その他",40,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},40,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ840HKXA     "," ",null,null,null,null,"その他",40,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},40,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,355,"FDCJ","FDCJ355HKX2A    "," ",null,null,null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},16.350000000000001,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,450,"FDCJ","FDCJ450HKX2A    "," ",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},20,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,140,"FDCJ","FDCJ140HKX2A    ","A",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,160,"FDCJ","FDCJ160HKX2A    ","A",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCJ","FDCJ224HKX2A    ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HKX2A    ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R407C","未分類",null,null,140,"FDCP","FDCP140HKX2A    ","A",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,160,"FDCP","FDCP160HKX2A    ","A",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,224,"FDCP","FDCP224HKX2A    ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCP","FDCP280HKX2A    ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,355,"FDCP","FDCP355HKX2A    "," ",null,null,null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},16.350000000000001,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,450,"FDCP","FDCP450HKX2A    "," ",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},20,"",0.27,0.46,0.49,""]
[null,"R22","未分類",null,null,224,"FDCJ","FDCJ224HKX2B-K  "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HKX2B-K  "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,224,"FDCSJ","FDCSJ224HKX2B-K "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,280,"FDCSJ","FDCSJ280HKX2B-K "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,224,"FDCP","FDCP224HKX2B-K  "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,280,"FDCP","FDCP280HKX2B-K  "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,224,"FDCP","FDCP224HKX2A-KT "," ",null,null,null,null,"その他",5,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},5,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,280,"FDCP","FDCP280HKX2A-KT "," ",null,null,null,null,"その他",7,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},7,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP225HKX2A-KT "," ",null,null,null,null,"その他",5,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},5,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP281HKX2A-KT "," ",null,null,null,null,"その他",7,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},7,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,224,"FDCSP","FDCSP224HKX2B-K "," ",null,null,null,null,"その他",5,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},5,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,280,"FDCSP","FDCSP280HKX2B-K "," ",null,null,null,null,"その他",7,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},7,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,224,"FDCSP","FDCSP224HKX2A-KT"," ",null,null,null,null,"その他",5,null,null,{"$f":"IF(Q135=\"\",\"\",IF(Q135=\"90m未満\",VLOOKUP(C135&D135&\",\"&F135,主管サイズルックアップ用,5,FALSE),VLOOKUP(C135&D135&\",\"&F135,主管サイズルックアップ用,6,FALSE)))","v":""},null,0.03,{"$f":"IF($R135=\"***\",\"実長90m超使用不可\",IF($R135<6.35,\"-主管サイズを超過-\",IF(T135=\"***\",\"0\",S135*T135)))","v":0},null,0.06,{"$f":"IF($R135=\"***\",\"実長90m超使用不可\",IF($R135<9.52,\"-主管サイズを超過-\",IF(W135=\"***\",\"0\",V135*W135)))","v":0},null,0.12,{"$f":"IF($R135=\"***\",\"実長90m超使用不可\",IF($R135<12.7,\"-主管サイズを超過-\",IF(Z135=\"***\",\"0\",Y135*Z135)))","v":0},null,0.2,{"$f":"IF($R135=\"***\",\"実長90m超使用不可\",IF($R135<15.88,\"-主管サイズを超過-\",IF(AC135=\"***\",\"0\",AB135*AC135)))","v":0},null,0.28000000000000003,{"$f":"IF($R135=\"***\",\"実長90m超使用不可\",IF($R135<19.05,\"-主管サイズを超過-\",IF(AF135=\"***\",\"0\",AE135*AF135)))","v":0},null,0.4,{"$f":"IF($R135=\"***\",\"実長90m超使用不可\",IF($R135<22.22,\"-主管サイズを超過-\",IF(AI135=\"***\",\"0\",AH135*AI135)))","v":0},null,0.53,{"$f":"IF($R135=\"***\",\"実長90m超使用不可\",IF($R135<25.4,\"-主管サイズを超過-\",IF(AL135=\"***\",\"0\",AK135*AL135)))","v":0},{"$f":"IF(OR(U135=\"実長90m超使用不可\",U135=\"-主管サイズを超過-\"),0,U135)+IF(OR(X135=\"実長90m超使用不可\",X135=\"-主管サイズを超過-\"),0,X135)+IF(OR(AA135=\"実長90m超使用不可\",AA135=\"-主管サイズを超過-\"),0,AA135)+IF(OR(AD135=\"実長90m超使用不可\",AD135=\"-主管サイズを超過-\"),0,AD135)+IF(OR(AG135=\"実長90m超使用不可\",AG135=\"-主管サイズを超過-\"),0,AG135)+IF(OR(AJ135=\"実長90m超使用不可\",AJ135=\"-主管サイズを超過-\"),0,AJ135)+IF(OR(AM135=\"実長90m超使用不可\",AM135=\"-主管サイズを超過-\"),0,AM135)","v":0},null,0,null,0,{"$f":"AR135","v":0},{"$f":"IF(AP135+AS135<0,0,AP135+AS135)","v":0},{"$f":"VLOOKUP(C135&D135&\",\"&F135,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},{"$f":"O135+AT135","v":5},{"$f":"IF(ISERROR(AV135/P135),\"\",AV135/P135)","v":""},{"$f":"IF(B135=\"R410A\",0.39,IF(B135=\"R407C\",0.27,IF(B135=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(B135=\"R410A\",0.42,IF(B135=\"R407C\",0.46,IF(B135=\"R22\",0.28,\"NG\")))","v":0.46},{"$f":"IF(B135=\"R410A\",0.42,IF(B135=\"R407C\",0.49,IF(B135=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(AW135=\"\",\"\",IF(OR(AW135<=AX135,AND(N135=\"その他\",AW135<=AY135)),\"OK\",IF(OR(AND(N135=\"最下層\",AW135<=AY135),AND(N135=\"その他\",AW135<=AZ135)),\"対策が１つ必要です\",IF(OR(AND(N135=\"最下層\",AW135<=AZ135),AND(N135=\"その他\",AW135>AZ135)),\"対策が２つ必要です\",\"システムの見直しが必要です\"))))","v":""},null,"組合せ専用機"]
[null,"R407C","未分類",null,null,280,"FDCSP","FDCSP280HKX2A-KT"," ",null,null,null,null,"その他",7,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,{"$f":"AN136*AO136","v":0},null,0,0,0,{"$error":"#N/A"},7,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP281HKX2A-KT"," ",null,null,null,null,"その他",5,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},5,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP225HKX2A-KT"," ",null,null,null,null,"その他",7,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},7,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,140,"FDCJ","FDCJ140HKX2B    "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,160,"FDCJ","FDCJ160HKX2B    "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCJ","FDCJ224HKX2B    "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HKX2B    "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,140,"FDCSJ","FDCSJ140HKX2B   "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,160,"FDCSJ","FDCSJ160HKX2B   "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCSJ","FDCSJ224HKX2B   "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCSJ","FDCSJ280HKX2B   "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R407C","未分類",null,null,140,"FDCP","FDCP140HKX2B    "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,160,"FDCP","FDCP160HKX2B    "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,224,"FDCP","FDCP224HKX2B    "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCP","FDCP280HKX2B    "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,140,"FDCSP","FDCSP140HKX2B   "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.27,0.46,{"$f":"IF(B151=\"R410A\",0.42,IF(B151=\"R407C\",0.49,IF(B151=\"R22\",0.5,\"NG\")))","v":0.49},""]
[null,"R407C","未分類",null,null,160,"FDCSP","FDCSP160HKX2B   "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.27,0.46,{"$f":"IF(B152=\"R410A\",0.42,IF(B152=\"R407C\",0.49,IF(B152=\"R22\",0.5,\"NG\")))","v":0.49},""]
[null,"R407C","未分類",null,null,224,"FDCSP","FDCSP224HKX2B   "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,{"$f":"IF(B153=\"R410A\",0.42,IF(B153=\"R407C\",0.49,IF(B153=\"R22\",0.5,\"NG\")))","v":0.49},""]
[null,"R407C","未分類",null,null,280,"FDCSP","FDCSP280HKX2B   "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,{"$f":"IF(B154=\"R410A\",0.42,IF(B154=\"R407C\",0.49,IF(B154=\"R22\",0.5,\"NG\")))","v":0.49},""]
[null,"R22","未分類",null,null,224,"FDCSJ","FDCSJ224HKXIB   "," ","ISU10HKX","FDCSJ224HKXIB   ",null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,1.2,1.2,1.2,{"$error":"#N/A"},13.2,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCSJ","FDCSJ280HKXIB   "," ","ISU13HKX","FDCSJ280HKXIB   ",null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,2.2000000000000002,2.2000000000000002,2.2000000000000002,{"$error":"#N/A"},14.2,"",0.21,0.28000000000000003,0.5,""]
[null,"R407C","未分類",null,null,355,"FDCSP","FDCSP355HKX2A   "," ",null,null,null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},16.350000000000001,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,450,"FDCSP","FDCSP450HKX2A   "," ",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,{"$f":"AR158","v":0},0,{"$error":"#N/A"},20,"",0.27,0.46,{"$f":"IF(B158=\"R410A\",0.42,IF(B158=\"R407C\",0.49,IF(B158=\"R22\",0.5,\"NG\")))","v":0.49},""]
[null,"R407C","未分類",null,null,140,"FDCSP","FDCSP140HKX2B-C "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.27,0.46,0.49,""]
[null,"R22","未分類",null,null,224,"FDCJ","FDCJ224HKX2D    "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,{"$f":"AR160","v":0},0,{"$error":"#N/A"},12,"",{"$f":"IF(B160=\"R410A\",0.39,IF(B160=\"R407C\",0.27,IF(B160=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B160=\"R410A\",0.42,IF(B160=\"R407C\",0.46,IF(B160=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(B160=\"R410A\",0.42,IF(B160=\"R407C\",0.49,IF(B160=\"R22\",0.5,\"NG\")))","v":0.5},""]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HKX2D    "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,{"$f":"AR161","v":0},0,{"$error":"#N/A"},12,"",{"$f":"IF(B161=\"R410A\",0.39,IF(B161=\"R407C\",0.27,IF(B161=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B161=\"R410A\",0.42,IF(B161=\"R407C\",0.46,IF(B161=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(B161=\"R410A\",0.42,IF(B161=\"R407C\",0.49,IF(B161=\"R22\",0.5,\"NG\")))","v":0.5},""]
[null,"R22","未分類",null,null,355,"FDCJ","FDCJ355HKX2D    "," ",null,null,null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},16.350000000000001,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,450,"FDCJ","FDCJ450HKX2D    "," ",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},20,"",0.21,0.28000000000000003,0.5,""]
[null,"R407C","未分類",null,null,355,"FDCP","FDCP355HKX2D    "," ",null,null,null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},16.350000000000001,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,450,"FDCP","FDCP450HKX2D    "," ",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,{"$f":"AR165","v":0},0,{"$error":"#N/A"},20,"",{"$f":"IF(B165=\"R410A\",0.39,IF(B165=\"R407C\",0.27,IF(B165=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(B165=\"R410A\",0.42,IF(B165=\"R407C\",0.46,IF(B165=\"R22\",0.28,\"NG\")))","v":0.46},{"$f":"IF(B165=\"R410A\",0.42,IF(B165=\"R407C\",0.49,IF(B165=\"R22\",0.5,\"NG\")))","v":0.49},""]
[null,"R22","未分類",null,null,224,"FDCJ","FDCJ224HKX2D-K  "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HKX2D-K  "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,224,"FDCSJ","FDCSJ224HKX2D-K "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,{"$f":"AR168","v":0},0,{"$error":"#N/A"},12,"",{"$f":"IF(B168=\"R410A\",0.39,IF(B168=\"R407C\",0.27,IF(B168=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B168=\"R410A\",0.42,IF(B168=\"R407C\",0.46,IF(B168=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(B168=\"R410A\",0.42,IF(B168=\"R407C\",0.49,IF(B168=\"R22\",0.5,\"NG\")))","v":0.5},"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,280,"FDCSJ","FDCSJ280HKX2D-K "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,{"$f":"AR169","v":0},0,{"$error":"#N/A"},12,"",{"$f":"IF(B169=\"R410A\",0.39,IF(B169=\"R407C\",0.27,IF(B169=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B169=\"R410A\",0.42,IF(B169=\"R407C\",0.46,IF(B169=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(B169=\"R410A\",0.42,IF(B169=\"R407C\",0.49,IF(B169=\"R22\",0.5,\"NG\")))","v":0.5},"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,224,"FDCP","FDCP224HKX2D-K  "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,280,"FDCP","FDCP280HKX2D-K  "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,224,"FDCSP","FDCSP224HKX2D-K "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,{"$f":"AR172","v":0},0,{"$error":"#N/A"},12,"",{"$f":"IF(B172=\"R410A\",0.39,IF(B172=\"R407C\",0.27,IF(B172=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(B172=\"R410A\",0.42,IF(B172=\"R407C\",0.46,IF(B172=\"R22\",0.28,\"NG\")))","v":0.46},{"$f":"IF(B172=\"R410A\",0.42,IF(B172=\"R407C\",0.49,IF(B172=\"R22\",0.5,\"NG\")))","v":0.49},"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,280,"FDCSP","FDCSP280HKX2D-K "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,{"$f":"AR173","v":0},0,{"$error":"#N/A"},12,"",{"$f":"IF(B173=\"R410A\",0.39,IF(B173=\"R407C\",0.27,IF(B173=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(B173=\"R410A\",0.42,IF(B173=\"R407C\",0.46,IF(B173=\"R22\",0.28,\"NG\")))","v":0.46},{"$f":"IF(B173=\"R410A\",0.42,IF(B173=\"R407C\",0.49,IF(B173=\"R22\",0.5,\"NG\")))","v":0.49},"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,224,"FDCSJ","FDCSJ224HKX2D   "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCSJ","FDCSJ280HKX2D   "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,{"$f":"AR175","v":0},0,{"$error":"#N/A"},12,"",{"$f":"IF(B175=\"R410A\",0.39,IF(B175=\"R407C\",0.27,IF(B175=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B175=\"R410A\",0.42,IF(B175=\"R407C\",0.46,IF(B175=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(B175=\"R410A\",0.42,IF(B175=\"R407C\",0.49,IF(B175=\"R22\",0.5,\"NG\")))","v":0.5},""]
[null,"R22","未分類",null,null,355,"FDCSJ","FDCSJ355HKX2D   "," ",null,null,null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},16.350000000000001,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,450,"FDCSJ","FDCSJ450HKX2D   "," ",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},20,"",0.21,0.28000000000000003,0.5,""]
[null,"R407C","未分類",null,null,355,"FDCSP","FDCSP355HKX2D   "," ",null,null,null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},16.350000000000001,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,450,"FDCSP","FDCSP450HKX2D   "," ",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},20,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,224,"FDCP","FDCP224HKX2D    "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCP","FDCP280HKX2D    "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,224,"FDCSP","FDCSP224HKX2D   "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCSP","FDCSP280HKX2D   "," ",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,{"$f":"AR183","v":0},0,{"$error":"#N/A"},12,"",{"$f":"IF(B183=\"R410A\",0.39,IF(B183=\"R407C\",0.27,IF(B183=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(B183=\"R410A\",0.42,IF(B183=\"R407C\",0.46,IF(B183=\"R22\",0.28,\"NG\")))","v":0.46},{"$f":"IF(B183=\"R410A\",0.42,IF(B183=\"R407C\",0.49,IF(B183=\"R22\",0.5,\"NG\")))","v":0.49},""]
[null,"R22","未分類",null,null,140,"FDCJ","FDCJ140HKX2D    "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,160,"FDCJ","FDCJ160HKX2D    "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,140,"FDCSJ","FDCSJ140HKX2D   "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,{"$f":"AR186","v":0},0,{"$error":"#N/A"},9,"",{"$f":"IF(B186=\"R410A\",0.39,IF(B186=\"R407C\",0.27,IF(B186=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B186=\"R410A\",0.42,IF(B186=\"R407C\",0.46,IF(B186=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(B186=\"R410A\",0.42,IF(B186=\"R407C\",0.49,IF(B186=\"R22\",0.5,\"NG\")))","v":0.5},""]
[null,"R22","未分類",null,null,160,"FDCSJ","FDCSJ160HKX2D   "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,{"$f":"AR187","v":0},0,{"$error":"#N/A"},9,"",{"$f":"IF(B187=\"R410A\",0.39,IF(B187=\"R407C\",0.27,IF(B187=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B187=\"R410A\",0.42,IF(B187=\"R407C\",0.46,IF(B187=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(B187=\"R410A\",0.42,IF(B187=\"R407C\",0.49,IF(B187=\"R22\",0.5,\"NG\")))","v":0.5},""]
[null,"R407C","未分類",null,null,140,"FDCP","FDCP140HKX2D    "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,160,"FDCP","FDCP160HKX2D    "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,140,"FDCSP","FDCSP140HKX2D   "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,160,"FDCSP","FDCSP160HKX2D   "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,224,"FDCP","FDCP224HKXRA    "," ",null,null,null,null,"その他",11,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCP","FDCP280HKXRA    "," ",null,null,null,null,"その他",11,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,560,"FDCP","FDCP560HKXRA    "," ",null,null,null,null,"その他",29,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},29,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,560,"FDCP","FDCP560HKXRA    ","A",null,null,null,null,"その他",29,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},29,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,224,"FDCSP","FDCSP224HKXRA   "," ",null,null,null,null,"その他",11,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCSP","FDCSP280HKXRA   "," ",null,null,null,null,"その他",11,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},11,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,560,"FDCSP","FDCSP560HKXRA   "," ",null,null,null,null,"その他",29,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},29,"",0.27,0.46,0.49,""]
[null,"R22","未分類",null,null,355,"FDCJ","FDCJ355HKXIS1   "," ","ISUJ450HS1","FDCJ355HKXIS1   ",null,null,"その他",20,null,null,{"$f":"IF(Q199=\"\",\"\",IF(Q199=\"90m未満\",VLOOKUP(C199&D199&\",\"&F199,主管サイズルックアップ用,5,FALSE),VLOOKUP(C199&D199&\",\"&F199,主管サイズルックアップ用,6,FALSE)))","v":""},null,0.03,{"$f":"IF($R199=\"***\",\"実長90m超使用不可\",IF($R199<6.35,\"-主管サイズを超過-\",IF(T199=\"***\",\"0\",S199*T199)))","v":0},null,0.06,{"$f":"IF($R199=\"***\",\"実長90m超使用不可\",IF($R199<9.52,\"-主管サイズを超過-\",IF(W199=\"***\",\"0\",V199*W199)))","v":0},null,0.12,{"$f":"IF($R199=\"***\",\"実長90m超使用不可\",IF($R199<12.7,\"-主管サイズを超過-\",IF(Z199=\"***\",\"0\",Y199*Z199)))","v":0},null,0.2,{"$f":"IF($R199=\"***\",\"実長90m超使用不可\",IF($R199<15.88,\"-主管サイズを超過-\",IF(AC199=\"***\",\"0\",AB199*AC199)))","v":0},null,0.28000000000000003,{"$f":"IF($R199=\"***\",\"実長90m超使用不可\",IF($R199<19.05,\"-主管サイズを超過-\",IF(AF199=\"***\",\"0\",AE199*AF199)))","v":0},null,"***",{"$f":"IF($R199=\"***\",\"実長90m超使用不可\",IF($R199<22.22,\"-主管サイズを超過-\",IF(AI199=\"***\",\"0\",AH199*AI199)))","v":"0"},null,"***",{"$f":"IF($R199=\"***\",\"実長90m超使用不可\",IF($R199<25.4,\"-主管サイズを超過-\",IF(AL199=\"***\",\"0\",AK199*AL199)))","v":"0"},{"$f":"IF(OR(U199=\"実長90m超使用不可\",U199=\"-主管サイズを超過-\"),0,U199)+IF(OR(X199=\"実長90m超使用不可\",X199=\"-主管サイズを超過-\"),0,X199)+IF(OR(AA199=\"実長90m超使用不可\",AA199=\"-主管サイズを超過-\"),0,AA199)+IF(OR(AD199=\"実長90m超使用不可\",AD199=\"-主管サイズを超過-\"),0,AD199)+IF(OR(AG199=\"実長90m超使用不可\",AG199=\"-主管サイズを超過-\"),0,AG199)+IF(OR(AJ199=\"実長90m超使用不可\",AJ199=\"-主管サイズを超過-\"),0,AJ199)+IF(OR(AM199=\"実長90m超使用不可\",AM199=\"-主管サイズを超過-\"),0,AM199)","v":0},null,0,null,26,{"$f":"AR199","v":26},{"$f":"IF(AP199+AS199<0,0,AP199+AS199)","v":26},{"$f":"VLOOKUP(C199&D199&\",\"&F199,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},{"$f":"O199+AT199","v":46},{"$f":"IF(ISERROR(AV199/P199),\"\",AV199/P199)","v":""},{"$f":"IF(B199=\"R410A\",0.39,IF(B199=\"R407C\",0.27,IF(B199=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B199=\"R410A\",0.42,IF(B199=\"R407C\",0.46,IF(B199=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(B199=\"R410A\",0.42,IF(B199=\"R407C\",0.49,IF(B199=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(AW199=\"\",\"\",IF(OR(AW199<=AX199,AND(N199=\"その他\",AW199<=AY199)),\"OK\",IF(OR(AND(N199=\"最下層\",AW199<=AY199),AND(N199=\"その他\",AW199<=AZ199)),\"対策が１つ必要です\",IF(OR(AND(N199=\"最下層\",AW199<=AZ199),AND(N199=\"その他\",AW199>AZ199)),\"対策が２つ必要です\",\"システムの見直しが必要です\"))))","v":""}]
[null,"R22","未分類",null,null,450,"FDCJ","FDCJ450HKXIS1   "," ","ISUJ560HS1","FDCJ450HKXIS1   ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,{"$f":"AN200*AO200","v":0},null,26,{"$f":"AR200","v":26},26,{"$error":"#N/A"},46,"",{"$f":"IF(B200=\"R410A\",0.39,IF(B200=\"R407C\",0.27,IF(B200=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B200=\"R410A\",0.42,IF(B200=\"R407C\",0.46,IF(B200=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,""]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HKXIS1A  "," ","ISUJ355HS1","FDCJ280HKXIS1A  ",null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,17,{"$f":"AR201","v":17},17,{"$error":"#N/A"},33.35,"",{"$f":"IF(B201=\"R410A\",0.39,IF(B201=\"R407C\",0.27,IF(B201=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B201=\"R410A\",0.42,IF(B201=\"R407C\",0.46,IF(B201=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,""]
[null,"R22","未分類",null,null,355,"FDCJ","FDCJ355HKXIS1A  "," ","ISUJ450HS1","FDCJ355HKXIS1A  ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,26,{"$f":"AR202","v":26},26,{"$error":"#N/A"},46,"",{"$f":"IF(B202=\"R410A\",0.39,IF(B202=\"R407C\",0.27,IF(B202=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B202=\"R410A\",0.42,IF(B202=\"R407C\",0.46,IF(B202=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,""]
[null,"R22","未分類",null,null,450,"FDCJ","FDCJ450HKXIS1A  "," ","ISUJ560HS1","FDCJ450HKXIS1A  ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,26,26,26,{"$error":"#N/A"},46,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HKXIS1A  ","B","ISUJ355HS1","FDCJ280HKXIS1A  ",null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,17,{"$f":"AR204","v":17},17,{"$error":"#N/A"},33.35,"",{"$f":"IF(B204=\"R410A\",0.39,IF(B204=\"R407C\",0.27,IF(B204=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B204=\"R410A\",0.42,IF(B204=\"R407C\",0.46,IF(B204=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(B204=\"R410A\",0.42,IF(B204=\"R407C\",0.49,IF(B204=\"R22\",0.5,\"NG\")))","v":0.5},""]
[null,"R22","未分類",null,null,355,"FDCJ","FDCJ355HKXIS1A  ","B","ISUJ450HS1","FDCJ355HKXIS1A  ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,26,{"$f":"AR205","v":26},26,{"$error":"#N/A"},46,"",{"$f":"IF(B205=\"R410A\",0.39,IF(B205=\"R407C\",0.27,IF(B205=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B205=\"R410A\",0.42,IF(B205=\"R407C\",0.46,IF(B205=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(B205=\"R410A\",0.42,IF(B205=\"R407C\",0.49,IF(B205=\"R22\",0.5,\"NG\")))","v":0.5},""]
[null,"R22","未分類",null,null,450,"FDCJ","FDCJ450HKXIS1A  ","B","ISUJ560HS1","FDCJ450HKXIS1A  ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,26,{"$f":"AR206","v":26},26,{"$error":"#N/A"},46,"",{"$f":"IF(B206=\"R410A\",0.39,IF(B206=\"R407C\",0.27,IF(B206=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B206=\"R410A\",0.42,IF(B206=\"R407C\",0.46,IF(B206=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(B206=\"R410A\",0.42,IF(B206=\"R407C\",0.49,IF(B206=\"R22\",0.5,\"NG\")))","v":0.5},""]
[null,"R22","未分類",null,null,280,"FDCSJ","FDCSJ280HKXIS1A "," ","ISUSJ355HS1","FDCSJ280HKXIS1A ",null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,17,{"$f":"AR207","v":17},17,{"$error":"#N/A"},33.35,"",{"$f":"IF(B207=\"R410A\",0.39,IF(B207=\"R407C\",0.27,IF(B207=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B207=\"R410A\",0.42,IF(B207=\"R407C\",0.46,IF(B207=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(B207=\"R410A\",0.42,IF(B207=\"R407C\",0.49,IF(B207=\"R22\",0.5,\"NG\")))","v":0.5},""]
[null,"R407C","未分類",null,null,280,"FDCP","FDCP280HKXIS1A  "," ","ISUP355HS1","FDCP280HKXIS1A  ",null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,17,17,17,{"$error":"#N/A"},33.35,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,355,"FDCP","FDCP355HKXIS1A  "," ","ISUP450HS1","FDCP355HKXIS1A  ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,26,26,26,{"$error":"#N/A"},46,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,450,"FDCP","FDCP450HKXIS1A  "," ","ISUP560HS1","FDCP450HKXIS1A  ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,26,26,26,{"$error":"#N/A"},46,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCP","FDCP280HKXIC1   "," ","ISUP355HC1","FDCP280HKXIC1   ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,19,19,19,{"$error":"#N/A"},39,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,355,"FDCP","FDCP355HKXIC1   "," ","ISUP450HC1","FDCP355HKXIC1   ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,22,22,22,{"$error":"#N/A"},42,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCSP","FDCSP280HKXIS1A "," ","ISUSP355HS1","FDCSP280HKXIS1A ",null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,17,17,17,{"$error":"#N/A"},33.35,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,355,"FDCSP","FDCSP355HKXIS1A "," ","ISUSP450HS1","FDCSP355HKXIS1A ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,26,26,26,{"$error":"#N/A"},46,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,450,"FDCSP","FDCSP450HKXIS1A "," ","ISUSP560HS1","FDCSP450HKXIS1A ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,26,26,26,{"$error":"#N/A"},46,"",0.27,0.46,0.49,""]
[null,"R22","未分類",null,null,160,"FDCJ","FDCJ160HKX2D    ","A",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,{"$f":"AR216","v":0},0,{"$error":"#N/A"},9,"",{"$f":"IF(B216=\"R410A\",0.39,IF(B216=\"R407C\",0.27,IF(B216=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B216=\"R410A\",0.42,IF(B216=\"R407C\",0.46,IF(B216=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,""]
[null,"R22","未分類",null,null,224,"FDCJ","FDCJ224HKX2D    ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HKX2D    ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",{"$f":"IF(B218=\"R410A\",0.39,IF(B218=\"R407C\",0.27,IF(B218=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B218=\"R410A\",0.42,IF(B218=\"R407C\",0.46,IF(B218=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,""]
[null,"R22","未分類",null,null,355,"FDCJ","FDCJ355HKX2D    ","A",null,null,null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},16.350000000000001,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,450,"FDCJ","FDCJ450HKX2D    ","A",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},20,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCSJ","FDCSJ224HKX2D   ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCSJ","FDCSJ280HKX2D   ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,355,"FDCSJ","FDCSJ355HKX2D   ","A",null,null,null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},16.350000000000001,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,450,"FDCSJ","FDCSJ450HKX2D   ","A",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},20,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCJ","FDCJ224HKX2D-K  ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HKX2D-K  ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,224,"FDCSJ","FDCSJ224HKX2D-K ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,280,"FDCSJ","FDCSJ280HKX2D-K ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,224,"FDCP","FDCP224HKX2D    ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCP","FDCP280HKX2D    ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,355,"FDCP","FDCP355HKX2D    ","A",null,null,null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},16.350000000000001,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,450,"FDCP","FDCP450HKX2D    ","A",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},20,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,224,"FDCSP","FDCSP224HKX2D   ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCSP","FDCSP280HKX2D   ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,355,"FDCSP","FDCSP355HKX2D   ","A",null,null,null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},16.350000000000001,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,450,"FDCSP","FDCSP450HKX2D   ","A",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},20,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,224,"FDCP","FDCP224HKX2D-K  ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,280,"FDCP","FDCP280HKX2D-K  ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,224,"FDCSP","FDCSP224HKX2D-K ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,280,"FDCSP","FDCSP280HKX2D-K ","A",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,224,"FDCJ","FDCJ224HKX2D    ","B",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HKX2D    ","B",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,355,"FDCJ","FDCJ355HKX2D    ","B",null,null,null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},16.350000000000001,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,450,"FDCJ","FDCJ450HKX2D    ","B",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},20,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCSJ","FDCSJ224HKX2D   ","B",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,280,"FDCSJ","FDCSJ280HKX2D   ","B",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,355,"FDCSJ","FDCSJ355HKX2D   ","B",null,null,null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},16.350000000000001,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,450,"FDCSJ","FDCSJ450HKX2D   ","B",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},20,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,224,"FDCJ","FDCJ224HKX2D-K  ","B",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,280,"FDCJ","FDCJ280HKX2D-K  ","B",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,224,"FDCSJ","FDCSJ224HKX2D-K ","B",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,280,"FDCSJ","FDCSJ280HKX2D-K ","B",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.21,0.28000000000000003,0.5,"",null,"組合せ専用機"]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ500HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ224HKX2A-KT ",null,null,"その他",{"$f":"12+5","v":17},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,560,"FDCJ","FDCJ560HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ280HKX2A-KT ",null,null,"その他",{"$f":"12+7","v":19},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},19,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ672HKX2DA  ",null,"FDCJ224HKX2D-K  ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ728HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ784HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ224HKX2A-KT ","FDCJ280HKX2A-KT ",null,"その他",{"$f":"12+5+7","v":24},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},24,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ840HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ280HKX2A-KT ","FDCJ280HKX2A-KT ",null,"その他",{"$f":"12+7+7","v":26},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},26,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ896HKX2DA  ",null,"FDCJ224HKX2D-K  ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ","その他",{"$f":"12+5+5+5","v":27},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},27,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ952HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ","その他",{"$f":"12+5+5+5","v":27},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},27,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ1008HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ","FDCJ280HKX2A-KT ","その他",{"$f":"12+5+5+7","v":29},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},29,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ1064HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ224HKX2A-KT ","FDCJ280HKX2A-KT ","FDCJ280HKX2A-KT ","その他",{"$f":"12+5+7+7","v":31},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},31,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ1120HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ280HKX2A-KT ","FDCJ280HKX2A-KT ","FDCJ280HKX2A-KT ","その他",{"$f":"12+7+7+7","v":33},null,null,{"$f":"IF(Q263=\"\",\"\",IF(Q263=\"90m未満\",VLOOKUP(C263&D263&\",\"&F263,主管サイズルックアップ用,5,FALSE),VLOOKUP(C263&D263&\",\"&F263,主管サイズルックアップ用,6,FALSE)))","v":""},null,0.03,{"$f":"IF($R263=\"***\",\"実長90m超使用不可\",IF($R263<6.35,\"-主管サイズを超過-\",IF(T263=\"***\",\"0\",S263*T263)))","v":0},null,0.06,{"$f":"IF($R263=\"***\",\"実長90m超使用不可\",IF($R263<9.52,\"-主管サイズを超過-\",IF(W263=\"***\",\"0\",V263*W263)))","v":0},null,0.12,{"$f":"IF($R263=\"***\",\"実長90m超使用不可\",IF($R263<12.7,\"-主管サイズを超過-\",IF(Z263=\"***\",\"0\",Y263*Z263)))","v":0},null,0.2,{"$f":"IF($R263=\"***\",\"実長90m超使用不可\",IF($R263<15.88,\"-主管サイズを超過-\",IF(AC263=\"***\",\"0\",AB263*AC263)))","v":0},null,0.28000000000000003,{"$f":"IF($R263=\"***\",\"実長90m超使用不可\",IF($R263<19.05,\"-主管サイズを超過-\",IF(AF263=\"***\",\"0\",AE263*AF263)))","v":0},null,0.4,{"$f":"IF($R263=\"***\",\"実長90m超使用不可\",IF($R263<22.22,\"-主管サイズを超過-\",IF(AI263=\"***\",\"0\",AH263*AI263)))","v":0},null,0.53,{"$f":"IF($R263=\"***\",\"実長90m超使用不可\",IF($R263<25.4,\"-主管サイズを超過-\",IF(AL263=\"***\",\"0\",AK263*AL263)))","v":0},{"$f":"IF(OR(U263=\"実長90m超使用不可\",U263=\"-主管サイズを超過-\"),0,U263)+IF(OR(X263=\"実長90m超使用不可\",X263=\"-主管サイズを超過-\"),0,X263)+IF(OR(AA263=\"実長90m超使用不可\",AA263=\"-主管サイズを超過-\"),0,AA263)+IF(OR(AD263=\"実長90m超使用不可\",AD263=\"-主管サイズを超過-\"),0,AD263)+IF(OR(AG263=\"実長90m超使用不可\",AG263=\"-主管サイズを超過-\"),0,AG263)+IF(OR(AJ263=\"実長90m超使用不可\",AJ263=\"-主管サイズを超過-\"),0,AJ263)+IF(OR(AM263=\"実長90m超使用不可\",AM263=\"-主管サイズを超過-\"),0,AM263)","v":0},null,0,null,0,0,{"$f":"IF(AP263+AS263<0,0,AP263+AS263)","v":0},{"$f":"VLOOKUP(C263&D263&\",\"&F263,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},{"$f":"O263+AT263","v":33},{"$f":"IF(ISERROR(AV263/P263),\"\",AV263/P263)","v":""},0.21,0.28000000000000003,{"$f":"IF(B263=\"R410A\",0.42,IF(B263=\"R407C\",0.49,IF(B263=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(AW263=\"\",\"\",IF(OR(AW263<=AX263,AND(N263=\"その他\",AW263<=AY263)),\"OK\",IF(OR(AND(N263=\"最下層\",AW263<=AY263),AND(N263=\"その他\",AW263<=AZ263)),\"対策が１つ必要です\",IF(OR(AND(N263=\"最下層\",AW263<=AZ263),AND(N263=\"その他\",AW263>AZ263)),\"対策が２つ必要です\",\"システムの見直しが必要です\"))))","v":""}]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ500HKX2DAF ",null,"FDCJ280HKX2D-K  ","FDCJ225HKX2A-KT ",null,null,"その他",{"$f":"12+5","v":17},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,{"$f":"AN264*AO264","v":0},null,0,0,0,{"$error":"#N/A"},17,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,560,"FDCJ","FDCJ560HKX2DAF  ",null,"FDCJ280HKX2D-K  ","FDCJ281HKX2A-KT ",null,null,"その他",{"$f":"12+7","v":19},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},19,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ672HKX2DAF  ",null,"FDCJ224HKX2D-K  ","FDCJ225HKX2A-KT ","FDCJ225HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,{"$f":"AR266","v":0},0,{"$error":"#N/A"},22,"",{"$f":"IF(B266=\"R410A\",0.39,IF(B266=\"R407C\",0.27,IF(B266=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(B266=\"R410A\",0.42,IF(B266=\"R407C\",0.46,IF(B266=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ728HKX2DAF  ",null,"FDCJ280HKX2D-K  ","FDCJ225HKX2A-KT ","FDCJ225HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ784HKX2DAF  ",null,"FDCJ280HKX2D-K  ","FDCJ225HKX2A-KT ","FDCJ281HKX2A-KT ",null,"その他",{"$f":"12+5+7","v":24},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},24,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ840HKX2DAF  ",null,"FDCJ280HKX2D-K  ","FDCJ281HKX2A-KT ","FDCJ281HKX2A-KT ",null,"その他",{"$f":"12+7+7","v":26},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},26,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ896HKX2DAF  ",null,"FDCJ224HKX2D-K  ","FDCJ225HKX2A-KT ","FDCJ225HKX2A-KT ","FDCJ225HKX2A-KT ","その他",{"$f":"12+5+5+5","v":27},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},27,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ952HKX2DAF  ",null,"FDCJ280HKX2D-K  ","FDCJ225HKX2A-KT ","FDCJ225HKX2A-KT ","FDCJ225HKX2A-KT ","その他",{"$f":"12+5+5+5","v":27},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},27,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ1008HKX2DAF  ",null,"FDCJ280HKX2D-K  ","FDCJ225HKX2A-KT ","FDCJ225HKX2A-KT ","FDCJ281HKX2A-KT ","その他",{"$f":"12+5+5+7","v":29},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},29,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ1064HKX2DAF  ",null,"FDCJ280HKX2D-K  ","FDCJ225HKX2A-KT ","FDCJ281HKX2A-KT ","FDCJ281HKX2A-KT ","その他",{"$f":"12+5+7+7","v":31},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},31,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCJ","FDCJ1120HKX2DAF  ",null,"FDCJ280HKX2D-K  ","FDCJ281HKX2A-KT ","FDCJ281HKX2A-KT ","FDCJ281HKX2A-KT ","その他",{"$f":"12+7+7+7","v":33},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},33,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ500HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ224HKX2A-KT ",null,null,"その他",{"$f":"12+5","v":17},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,560,"FDCSJ","FDCSJ560HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ280HKX2A-KT ",null,null,"その他",{"$f":"12+7","v":19},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},19,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ672HKX2DA  ",null,"FDCSJ224HKX2D-K  ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ728HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ784HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ224HKX2A-KT ","FDCSJ280HKX2A-KT ",null,"その他",{"$f":"12+5+7","v":24},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},24,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ840HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ280HKX2A-KT ","FDCSJ280HKX2A-KT ",null,"その他",{"$f":"12+7+7","v":26},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},26,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ896HKX2DA  ",null,"FDCSJ224HKX2D-K  ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ","その他",{"$f":"12+5+5+5","v":27},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},27,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ952HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ","その他",{"$f":"12+5+5+5","v":27},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},27,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ1008HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ","FDCSJ280HKX2A-KT ","その他",{"$f":"12+5+5+7","v":29},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},29,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ1064HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ224HKX2A-KT ","FDCSJ280HKX2A-KT ","FDCSJ280HKX2A-KT ","その他",{"$f":"12+5+7+7","v":31},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},31,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ1120HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ280HKX2A-KT ","FDCSJ280HKX2A-KT ","FDCSJ280HKX2A-KT ","その他",{"$f":"12+7+7+7","v":33},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},33,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ500HKX2DAF ",null,"FDCSJ280HKX2D-K  ","FDCSJ225HKX2A-KT ",null,null,"その他",{"$f":"12+5","v":17},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,560,"FDCSJ","FDCSJ560HKX2DAF  ",null,"FDCSJ280HKX2D-K  ","FDCSJ281HKX2A-KT ",null,null,"その他",{"$f":"12+7","v":19},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},19,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ672HKX2DAF  ",null,"FDCSJ224HKX2D-K  ","FDCSJ225HKX2A-KT ","FDCSJ225HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ728HKX2DAF  ",null,"FDCSJ280HKX2D-K  ","FDCSJ225HKX2A-KT ","FDCSJ225HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ784HKX2DAF  ",null,"FDCSJ280HKX2D-K  ","FDCSJ225HKX2A-KT ","FDCSJ281HKX2A-KT ",null,"その他",{"$f":"12+5+7","v":24},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},24,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ840HKX2DAF  ",null,"FDCSJ280HKX2D-K  ","FDCSJ281HKX2A-KT ","FDCSJ281HKX2A-KT ",null,"その他",{"$f":"12+7+7","v":26},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},26,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ896HKX2DAF  ",null,"FDCSJ224HKX2D-K  ","FDCSJ225HKX2A-KT ","FDCSJ225HKX2A-KT ","FDCSJ225HKX2A-KT ","その他",{"$f":"12+5+5+5","v":27},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},27,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ952HKX2DAF  ",null,"FDCSJ280HKX2D-K  ","FDCSJ225HKX2A-KT ","FDCSJ225HKX2A-KT ","FDCSJ225HKX2A-KT ","その他",{"$f":"12+5+5+5","v":27},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},27,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ1008HKX2DAF  ",null,"FDCSJ280HKX2D-K  ","FDCSJ225HKX2A-KT ","FDCSJ225HKX2A-KT ","FDCSJ281HKX2A-KT ","その他",{"$f":"12+5+5+7","v":29},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},29,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ1064HKX2DAF  ",null,"FDCSJ280HKX2D-K  ","FDCSJ225HKX2A-KT ","FDCSJ281HKX2A-KT ","FDCSJ281HKX2A-KT ","その他",{"$f":"12+5+7+7","v":31},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},31,"",0.21,0.28000000000000003,0.5,""]
[null,"R22","未分類",null,null,null,"FDCSJ","FDCSJ1120HKX2DAF  ",null,"FDCSJ280HKX2D-K  ","FDCSJ281HKX2A-KT ","FDCSJ281HKX2A-KT ","FDCSJ281HKX2A-KT ","その他",{"$f":"12+7+7+7","v":33},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},33,"",0.21,0.28000000000000003,0.5,""]
[null,"R407C","未分類",null,null,224,"FDCP","FDCP224HKX2D    ","B",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCP","FDCP280HKX2D    ","B",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,355,"FDCP","FDCP355HKX2D    ","B",null,null,null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},16.350000000000001,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,450,"FDCP","FDCP450HKX2D    ","B",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},20,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,224,"FDCSP","FDCSP224HKX2D   ","B",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCSP","FDCSP280HKX2D   ","B",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,355,"FDCSP","FDCSP355HKX2D   ","B",null,null,null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},16.350000000000001,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,450,"FDCSP","FDCSP450HKX2D   ","B",null,null,null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},20,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,224,"FDCP","FDCP224HKX2D-K  ","B",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,280,"FDCP","FDCP280HKX2D-K  ","B",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,224,"FDCSP","FDCSP224HKX2D-K ","B",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,280,"FDCSP","FDCSP280HKX2D-K ","B",null,null,null,null,"その他",12,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},12,"",0.27,0.46,0.49,"",null,"組合せ専用機"]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP500HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP224HKX2A-KT ",null,null,"その他",{"$f":"12+5","v":17},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,560,"FDCP","FDCP560HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP280HKX2A-KT ",null,null,"その他",{"$f":"12+7","v":19},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},19,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP672HKX2DA  ",null,"FDCP224HKX2D-K  ","FDCP224HKX2A-KT ","FDCP224HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP728HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP224HKX2A-KT ","FDCP224HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP784HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP224HKX2A-KT ","FDCP280HKX2A-KT ",null,"その他",{"$f":"12+5+7","v":24},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},24,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP840HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP280HKX2A-KT ","FDCP280HKX2A-KT ",null,"その他",{"$f":"12+7+7","v":26},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},26,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP896HKX2DA  ",null,"FDCP224HKX2D-K  ","FDCP224HKX2A-KT ","FDCP224HKX2A-KT ","FDCP224HKX2A-KT ","その他",{"$f":"12+5+5+5","v":27},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},27,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP952HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP224HKX2A-KT ","FDCP224HKX2A-KT ","FDCP224HKX2A-KT ","その他",{"$f":"12+5+5+5","v":27},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},27,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP1008HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP224HKX2A-KT ","FDCP224HKX2A-KT ","FDCP280HKX2A-KT ","その他",{"$f":"12+5+5+7","v":29},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},29,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP1064HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP224HKX2A-KT ","FDCP280HKX2A-KT ","FDCP280HKX2A-KT ","その他",{"$f":"12+5+7+7","v":31},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},31,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP1120HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP280HKX2A-KT ","FDCP280HKX2A-KT ","FDCP280HKX2A-KT ","その他",{"$f":"12+7+7+7","v":33},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},33,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP500HKX2DAF ",null,"FDCP280HKX2D-K  ","FDCP225HKX2A-KT ",null,null,"その他",{"$f":"12+5","v":17},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,560,"FDCP","FDCP560HKX2DAF  ",null,"FDCP280HKX2D-K  ","FDCP281HKX2A-KT ",null,null,"その他",{"$f":"12+7","v":19},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},19,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP672HKX2DAF  ",null,"FDCP224HKX2D-K  ","FDCP225HKX2A-KT ","FDCP225HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP728HKX2DAF  ",null,"FDCP280HKX2D-K  ","FDCP225HKX2A-KT ","FDCP225HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP784HKX2DAF  ",null,"FDCP280HKX2D-K  ","FDCP225HKX2A-KT ","FDCP281HKX2A-KT ",null,"その他",{"$f":"12+5+7","v":24},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},24,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP840HKX2DAF  ",null,"FDCP280HKX2D-K  ","FDCP281HKX2A-KT ","FDCP281HKX2A-KT ",null,"その他",{"$f":"12+7+7","v":26},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},26,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP896HKX2DAF  ",null,"FDCP224HKX2D-K  ","FDCP225HKX2A-KT ","FDCP225HKX2A-KT ","FDCP225HKX2A-KT ","その他",{"$f":"12+5+5+5","v":27},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},27,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP952HKX2DAF  ",null,"FDCP280HKX2D-K  ","FDCP225HKX2A-KT ","FDCP225HKX2A-KT ","FDCP225HKX2A-KT ","その他",{"$f":"12+5+5+5","v":27},null,null,{"$f":"IF(Q327=\"\",\"\",IF(Q327=\"90m未満\",VLOOKUP(C327&D327&\",\"&F327,主管サイズルックアップ用,5,FALSE),VLOOKUP(C327&D327&\",\"&F327,主管サイズルックアップ用,6,FALSE)))","v":""},null,0.03,{"$f":"IF($R327=\"***\",\"実長90m超使用不可\",IF($R327<6.35,\"-主管サイズを超過-\",IF(T327=\"***\",\"0\",S327*T327)))","v":0},null,0.06,{"$f":"IF($R327=\"***\",\"実長90m超使用不可\",IF($R327<9.52,\"-主管サイズを超過-\",IF(W327=\"***\",\"0\",V327*W327)))","v":0},null,0.12,{"$f":"IF($R327=\"***\",\"実長90m超使用不可\",IF($R327<12.7,\"-主管サイズを超過-\",IF(Z327=\"***\",\"0\",Y327*Z327)))","v":0},null,0.2,{"$f":"IF($R327=\"***\",\"実長90m超使用不可\",IF($R327<15.88,\"-主管サイズを超過-\",IF(AC327=\"***\",\"0\",AB327*AC327)))","v":0},null,0.28000000000000003,{"$f":"IF($R327=\"***\",\"実長90m超使用不可\",IF($R327<19.05,\"-主管サイズを超過-\",IF(AF327=\"***\",\"0\",AE327*AF327)))","v":0},null,0.4,{"$f":"IF($R327=\"***\",\"実長90m超使用不可\",IF($R327<22.22,\"-主管サイズを超過-\",IF(AI327=\"***\",\"0\",AH327*AI327)))","v":0},null,0.53,{"$f":"IF($R327=\"***\",\"実長90m超使用不可\",IF($R327<25.4,\"-主管サイズを超過-\",IF(AL327=\"***\",\"0\",AK327*AL327)))","v":0},{"$f":"IF(OR(U327=\"実長90m超使用不可\",U327=\"-主管サイズを超過-\"),0,U327)+IF(OR(X327=\"実長90m超使用不可\",X327=\"-主管サイズを超過-\"),0,X327)+IF(OR(AA327=\"実長90m超使用不可\",AA327=\"-主管サイズを超過-\"),0,AA327)+IF(OR(AD327=\"実長90m超使用不可\",AD327=\"-主管サイズを超過-\"),0,AD327)+IF(OR(AG327=\"実長90m超使用不可\",AG327=\"-主管サイズを超過-\"),0,AG327)+IF(OR(AJ327=\"実長90m超使用不可\",AJ327=\"-主管サイズを超過-\"),0,AJ327)+IF(OR(AM327=\"実長90m超使用不可\",AM327=\"-主管サイズを超過-\"),0,AM327)","v":0},null,0,null,0,0,{"$f":"IF(AP327+AS327<0,0,AP327+AS327)","v":0},{"$f":"VLOOKUP(C327&D327&\",\"&F327,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},{"$f":"O327+AT327","v":27},{"$f":"IF(ISERROR(AV327/P327),\"\",AV327/P327)","v":""},0.27,0.46,{"$f":"IF(B327=\"R410A\",0.42,IF(B327=\"R407C\",0.49,IF(B327=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(AW327=\"\",\"\",IF(OR(AW327<=AX327,AND(N327=\"その他\",AW327<=AY327)),\"OK\",IF(OR(AND(N327=\"最下層\",AW327<=AY327),AND(N327=\"その他\",AW327<=AZ327)),\"対策が１つ必要です\",IF(OR(AND(N327=\"最下層\",AW327<=AZ327),AND(N327=\"その他\",AW327>AZ327)),\"対策が２つ必要です\",\"システムの見直しが必要です\"))))","v":""}]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP1008HKX2DAF  ",null,"FDCP280HKX2D-K  ","FDCP225HKX2A-KT ","FDCP225HKX2A-KT ","FDCP281HKX2A-KT ","その他",{"$f":"12+5+5+7","v":29},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,{"$f":"AN328*AO328","v":0},null,0,0,0,{"$error":"#N/A"},29,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP1064HKX2DAF  ",null,"FDCP280HKX2D-K  ","FDCP225HKX2A-KT ","FDCP281HKX2A-KT ","FDCP281HKX2A-KT ","その他",{"$f":"12+5+7+7","v":31},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},31,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCP","FDCP1120HKX2DAF  ",null,"FDCP280HKX2D-K  ","FDCP281HKX2A-KT ","FDCP281HKX2A-KT ","FDCP281HKX2A-KT ","その他",{"$f":"12+7+7+7","v":33},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,{"$f":"AR330","v":0},0,{"$error":"#N/A"},33,"",{"$f":"IF(B330=\"R410A\",0.39,IF(B330=\"R407C\",0.27,IF(B330=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(B330=\"R410A\",0.42,IF(B330=\"R407C\",0.46,IF(B330=\"R22\",0.28,\"NG\")))","v":0.46},0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP500HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP224HKX2A-KT ",null,null,"その他",{"$f":"12+5","v":17},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,560,"FDCSP","FDCSP560HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP280HKX2A-KT ",null,null,"その他",{"$f":"12+7","v":19},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},19,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP672HKX2DA  ",null,"FDCSP224HKX2D-K  ","FDCSP224HKX2A-KT ","FDCSP224HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP728HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP224HKX2A-KT ","FDCSP224HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP784HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP224HKX2A-KT ","FDCSP280HKX2A-KT ",null,"その他",{"$f":"12+5+7","v":24},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},24,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP840HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP280HKX2A-KT ","FDCSP280HKX2A-KT ",null,"その他",{"$f":"12+7+7","v":26},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},26,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP896HKX2DA  ",null,"FDCSP224HKX2D-K  ","FDCSP224HKX2A-KT ","FDCSP224HKX2A-KT ","FDCSP224HKX2A-KT ","その他",{"$f":"12+5+5+5","v":27},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},27,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP952HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP224HKX2A-KT ","FDCSP224HKX2A-KT ","FDCSP224HKX2A-KT ","その他",{"$f":"12+5+5+5","v":27},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},27,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP1008HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP224HKX2A-KT ","FDCSP224HKX2A-KT ","FDCSP280HKX2A-KT ","その他",{"$f":"12+5+5+7","v":29},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},29,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP1064HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP224HKX2A-KT ","FDCSP280HKX2A-KT ","FDCSP280HKX2A-KT ","その他",{"$f":"12+5+7+7","v":31},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},31,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP1120HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP280HKX2A-KT ","FDCSP280HKX2A-KT ","FDCSP280HKX2A-KT ","その他",{"$f":"12+7+7+7","v":33},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},33,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP500HKX2DAF ",null,"FDCSP280HKX2D-K  ","FDCSP225HKX2A-KT ",null,null,"その他",{"$f":"12+5","v":17},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,560,"FDCSP","FDCSP560HKX2DAF  ",null,"FDCSP280HKX2D-K  ","FDCSP281HKX2A-KT ",null,null,"その他",{"$f":"12+7","v":19},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},19,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP672HKX2DAF  ",null,"FDCSP224HKX2D-K  ","FDCSP225HKX2A-KT ","FDCSP225HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP728HKX2DAF  ",null,"FDCSP280HKX2D-K  ","FDCSP225HKX2A-KT ","FDCSP225HKX2A-KT ",null,"その他",{"$f":"12+5+5","v":22},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},22,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP784HKX2DAF  ",null,"FDCSP280HKX2D-K  ","FDCSP225HKX2A-KT ","FDCSP281HKX2A-KT ",null,"その他",{"$f":"12+5+7","v":24},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},24,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP840HKX2DAF  ",null,"FDCSP280HKX2D-K  ","FDCSP281HKX2A-KT ","FDCSP281HKX2A-KT ",null,"その他",{"$f":"12+7+7","v":26},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},26,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP896HKX2DAF  ",null,"FDCSP224HKX2D-K  ","FDCSP225HKX2A-KT ","FDCSP225HKX2A-KT ","FDCSP225HKX2A-KT ","その他",{"$f":"12+5+5+5","v":27},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},27,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP952HKX2DAF  ",null,"FDCSP280HKX2D-K  ","FDCSP225HKX2A-KT ","FDCSP225HKX2A-KT ","FDCSP225HKX2A-KT ","その他",{"$f":"12+5+5+5","v":27},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},27,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP1008HKX2DAF  ",null,"FDCSP280HKX2D-K  ","FDCSP225HKX2A-KT ","FDCSP225HKX2A-KT ","FDCSP281HKX2A-KT ","その他",{"$f":"12+5+5+7","v":29},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},29,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP1064HKX2DAF  ",null,"FDCSP280HKX2D-K  ","FDCSP225HKX2A-KT ","FDCSP281HKX2A-KT ","FDCSP281HKX2A-KT ","その他",{"$f":"12+5+7+7","v":31},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},31,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,null,"FDCSP","FDCSP1120HKX2DAF  ",null,"FDCSP280HKX2D-K  ","FDCSP281HKX2A-KT ","FDCSP281HKX2A-KT ","FDCSP281HKX2A-KT ","その他",{"$f":"12+7+7+7","v":33},null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,0.4,0,null,0.53,0,0,null,0,null,0,0,0,{"$error":"#N/A"},33,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCP","FDCP280HKXIC1   ","B","ISUP355HC1","FDCP280HKXIC1   ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,19,19,19,{"$error":"#N/A"},39,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,355,"FDCP","FDCP355HKXIC1   ","B","ISUP450HC1","FDCP355HKXIC1   ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,22,22,22,{"$error":"#N/A"},42,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCSP","FDCSP280HKXIC1  ","B","ISUSP355HC1","FDCSP280HKXIC1  ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,19,{"$f":"AR355","v":19},19,{"$error":"#N/A"},39,"",{"$f":"IF(B355=\"R410A\",0.39,IF(B355=\"R407C\",0.27,IF(B355=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(B355=\"R410A\",0.42,IF(B355=\"R407C\",0.46,IF(B355=\"R22\",0.28,\"NG\")))","v":0.46},{"$f":"IF(B355=\"R410A\",0.42,IF(B355=\"R407C\",0.49,IF(B355=\"R22\",0.5,\"NG\")))","v":0.49},""]
[null,"R407C","未分類",null,null,355,"FDCSP","FDCSP355HKXIC1  ","B","ISUSP450HC1","FDCSP355HKXIC1  ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,22,{"$f":"AR356","v":22},22,{"$error":"#N/A"},42,"",{"$f":"IF(B356=\"R410A\",0.39,IF(B356=\"R407C\",0.27,IF(B356=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(B356=\"R410A\",0.42,IF(B356=\"R407C\",0.46,IF(B356=\"R22\",0.28,\"NG\")))","v":0.46},{"$f":"IF(B356=\"R410A\",0.42,IF(B356=\"R407C\",0.49,IF(B356=\"R22\",0.5,\"NG\")))","v":0.49},""]
[null,"R407C","未分類",null,null,280,"FDCSP","FDCSP280HKXIC1  ","C","ISUSP355HC1","FDCSP280HKXIC1  ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,19,{"$f":"AR357","v":19},19,{"$error":"#N/A"},39,"",{"$f":"IF(B357=\"R410A\",0.39,IF(B357=\"R407C\",0.27,IF(B357=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(B357=\"R410A\",0.42,IF(B357=\"R407C\",0.46,IF(B357=\"R22\",0.28,\"NG\")))","v":0.46},{"$f":"IF(B357=\"R410A\",0.42,IF(B357=\"R407C\",0.49,IF(B357=\"R22\",0.5,\"NG\")))","v":0.49},""]
[null,"R407C","未分類",null,null,355,"FDCSP","FDCSP355HKXIC1  ","C","ISUSP450HC1","FDCSP355HKXIC1  ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,22,{"$f":"AR358","v":22},22,{"$error":"#N/A"},42,"",{"$f":"IF(B358=\"R410A\",0.39,IF(B358=\"R407C\",0.27,IF(B358=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(B358=\"R410A\",0.42,IF(B358=\"R407C\",0.46,IF(B358=\"R22\",0.28,\"NG\")))","v":0.46},{"$f":"IF(B358=\"R410A\",0.42,IF(B358=\"R407C\",0.49,IF(B358=\"R22\",0.5,\"NG\")))","v":0.49},""]
[null,"R407C","未分類",null,null,280,"FDCP","FDCP280HKXIS1A  ","B","ISUP355HS1","FDCP280HKXIS1A  ",null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,17,{"$f":"AR359","v":17},17,{"$error":"#N/A"},33.35,"",{"$f":"IF(B359=\"R410A\",0.39,IF(B359=\"R407C\",0.27,IF(B359=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(B359=\"R410A\",0.42,IF(B359=\"R407C\",0.46,IF(B359=\"R22\",0.28,\"NG\")))","v":0.46},0.49,""]
[null,"R407C","未分類",null,null,355,"FDCP","FDCP355HKXIS1A  ","B","ISUP450HS1","FDCP355HKXIS1A  ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,26,26,26,{"$error":"#N/A"},46,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,450,"FDCP","FDCP450HKXIS1A  ","B","ISUP560HS1","FDCP450HKXIS1A  ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,26,26,26,{"$error":"#N/A"},46,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCSP","FDCSP280HKXIS1A ","B","ISUSP355HS1","FDCSP280HKXIS1A ",null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,17,17,17,{"$error":"#N/A"},33.35,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,355,"FDCSP","FDCSP355HKXIS1A ","B","ISUSP450HS1","FDCSP355HKXIS1A ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,26,26,26,{"$error":"#N/A"},46,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,450,"FDCSP","FDCSP450HKXIS1A ","B","ISUSP560HS1","FDCSP450HKXIS1A ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,26,26,26,{"$error":"#N/A"},46,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCSP","FDCSP280HKXIS1A ","C","ISUSP355HS1","FDCSP280HKXIS1A ",null,null,"その他",16.350000000000001,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,17,17,17,{"$error":"#N/A"},33.35,"",0.27,0.46,{"$f":"IF(B365=\"R410A\",0.42,IF(B365=\"R407C\",0.49,IF(B365=\"R22\",0.5,\"NG\")))","v":0.49},""]
[null,"R407C","未分類",null,null,355,"FDCSP","FDCSP355HKXIS1A ","C","ISUSP450HS1","FDCSP355HKXIS1A ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,26,26,26,{"$error":"#N/A"},46,"",0.27,0.46,{"$f":"IF(B366=\"R410A\",0.42,IF(B366=\"R407C\",0.49,IF(B366=\"R22\",0.5,\"NG\")))","v":0.49},""]
[null,"R407C","未分類",null,null,450,"FDCSP","FDCSP450HKXIS1A ","C","ISUSP560HS1","FDCSP450HKXIS1A ",null,null,"その他",20,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,0.2,0,null,0.28000000000000003,0,null,"***","0",null,"***","0",0,null,0,null,26,26,26,{"$error":"#N/A"},46,"",0.27,0.46,{"$f":"IF(B367=\"R410A\",0.42,IF(B367=\"R407C\",0.49,IF(B367=\"R22\",0.5,\"NG\")))","v":0.49},""]
[null,"R407C","未分類",null,null,140,"FDCP","FDCP140HKX2DA   "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,140,"FDCSP","FDCSP140HKX2DA  "," ",null,null,null,null,"その他",9,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},9,"",0.27,0.46,{"$f":"IF(B369=\"R410A\",0.42,IF(B369=\"R407C\",0.49,IF(B369=\"R22\",0.5,\"NG\")))","v":0.49},""]
[null,"R407C","未分類",null,null,224,"FDCP","FDCP224HKX3     "," ",null,null,null,null,"その他",14,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14,"",0.27,0.46,0.49,""]
[null,"R407C","未分類",null,null,280,"FDCP","FDCP280HKX3     "," ",null,null,null,null,"その他",14,null,null,"",null,0.03,0,null,0.06,0,null,0.12,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14,"",0.27,0.46,0.49,""]
[null,"R410A",1,null,null,140,"FDCP","FDCP1401HLX     "," ",null,null,null,null,"その他",8.5,null,null,"",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},8.5,"",0.39,0.42,{"$f":"IF(B372=\"R410A\",0.42,IF(B372=\"R407C\",0.49,IF(B372=\"R22\",0.5,\"NG\")))","v":0.42},""]
[null,"R410A",1,null,null,160,"FDCP","FDCP1601HLX     "," ",null,null,null,null,"その他",8.5,null,null,"",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},8.5,"",0.39,0.42,{"$f":"IF(B373=\"R410A\",0.42,IF(B373=\"R407C\",0.49,IF(B373=\"R22\",0.5,\"NG\")))","v":0.42},""]
[null,"R410A",1,null,null,224,"FDCP","FDCP2241HLX     "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,280,"FDCP","FDCP2801HLX     "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,335,"FDCP","FDCP3351HLX     "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,335,"FDCP","FDCP3351HLX-K   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,400,"FDCP","FDCP4001HLX     "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,450,"FDCP","FDCP4501HLX     "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,504,"FDCP","FDCP5041HLX     "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,560,"FDCP","FDCP5601HLX     "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,615,"FDCP","FDCP6151HLX     "," ",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,680,"FDCP","FDCP6801HLX     "," ",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,735,"FDCP","FDCP7351HLX",null,"FDCP3351HLX-K   ","FDCP4001HLX     ",null,null,"その他",{"$f":"O377+O378","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,800,"FDCP","FDCP8001HLX",null,"FDCP4001HLX     ","FDCP4001HLX     ",null,null,"その他",{"$f":"O378+O378","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,850,"FDCP","FDCP8501HLX",null,"FDCP4001HLX     ","FDCP4501HLX     ",null,null,"その他",{"$f":"O378+O379","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,900,"FDCP","FDCP9001HLX",null,"FDCP4501HLX     ","FDCP4501HLX     ",null,null,"その他",{"$f":"O379+O379","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,960,"FDCP","FDCP9601HLX",null,"FDCP4501HLX     ","FDCP5041HLX     ",null,null,"その他",{"$f":"O379+O380","v":36.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},36.4,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,1010,"FDCP","FDCP10101HLX",null,"FDCP5041HLX     ","FDCP5041HLX     ",null,null,"その他",{"$f":"O380+O380","v":38.799999999999997},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},38.799999999999997,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,1065,"FDCP","FDCP10651HLX",null,"FDCP5041HLX     ","FDCP5601HLX     ",null,null,"その他",{"$f":"O380+O381","v":38.799999999999997},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},38.799999999999997,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,1130,"FDCP","FDCP11301HLX",null,"FDCP5601HLX     ","FDCP5601HLX     ",null,null,"その他",{"$f":"O381+O381","v":38.799999999999997},null,null,{"$f":"IF(Q391=\"\",\"\",IF(Q391=\"90m未満\",VLOOKUP(C391&D391&\",\"&F391,主管サイズルックアップ用,5,FALSE),VLOOKUP(C391&D391&\",\"&F391,主管サイズルックアップ用,6,FALSE)))","v":""},null,2.1999999999999999E-2,{"$f":"IF($R391=\"***\",\"実長90m超使用不可\",IF($R391<6.35,\"-主管サイズを超過-\",IF(T391=\"***\",\"0\",S391*T391)))","v":0},null,5.3999999999999999E-2,{"$f":"IF($R391=\"***\",\"実長90m超使用不可\",IF($R391<9.52,\"-主管サイズを超過-\",IF(W391=\"***\",\"0\",V391*W391)))","v":0},null,0.11,{"$f":"IF($R391=\"***\",\"実長90m超使用不可\",IF($R391<12.7,\"-主管サイズを超過-\",IF(Z391=\"***\",\"0\",Y391*Z391)))","v":0},null,0.17,{"$f":"IF($R391=\"***\",\"実長90m超使用不可\",IF($R391<15.88,\"-主管サイズを超過-\",IF(AC391=\"***\",\"0\",AB391*AC391)))","v":0},null,0.25,{"$f":"IF($R391=\"***\",\"実長90m超使用不可\",IF($R391<19.05,\"-主管サイズを超過-\",IF(AF391=\"***\",\"0\",AE391*AF391)))","v":0},null,0.35,{"$f":"IF($R391=\"***\",\"実長90m超使用不可\",IF($R391<22.22,\"-主管サイズを超過-\",IF(AI391=\"***\",\"0\",AH391*AI391)))","v":0},null,"***",{"$f":"IF($R391=\"***\",\"実長90m超使用不可\",IF($R391<25.4,\"-主管サイズを超過-\",IF(AL391=\"***\",\"0\",AK391*AL391)))","v":"0"},{"$f":"IF(OR(U391=\"実長90m超使用不可\",U391=\"-主管サイズを超過-\"),0,U391)+IF(OR(X391=\"実長90m超使用不可\",X391=\"-主管サイズを超過-\"),0,X391)+IF(OR(AA391=\"実長90m超使用不可\",AA391=\"-主管サイズを超過-\"),0,AA391)+IF(OR(AD391=\"実長90m超使用不可\",AD391=\"-主管サイズを超過-\"),0,AD391)+IF(OR(AG391=\"実長90m超使用不可\",AG391=\"-主管サイズを超過-\"),0,AG391)+IF(OR(AJ391=\"実長90m超使用不可\",AJ391=\"-主管サイズを超過-\"),0,AJ391)+IF(OR(AM391=\"実長90m超使用不可\",AM391=\"-主管サイズを超過-\"),0,AM391)","v":0},null,0,null,0,0,{"$f":"IF(AP391+AS391<0,0,AP391+AS391)","v":0},{"$f":"VLOOKUP(C391&D391&\",\"&F391,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},{"$f":"O391+AT391","v":38.799999999999997},{"$f":"IF(ISERROR(AV391/P391),\"\",AV391/P391)","v":""},0.39,0.42,{"$f":"IF(B391=\"R410A\",0.42,IF(B391=\"R407C\",0.49,IF(B391=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(AW391=\"\",\"\",IF(OR(AW391<=AX391,AND(N391=\"その他\",AW391<=AY391)),\"OK\",IF(OR(AND(N391=\"最下層\",AW391<=AY391),AND(N391=\"その他\",AW391<=AZ391)),\"対策が１つ必要です\",IF(OR(AND(N391=\"最下層\",AW391<=AZ391),AND(N391=\"その他\",AW391>AZ391)),\"対策が２つ必要です\",\"システムの見直しが必要です\"))))","v":""}]
[null,"R410A",1,null,null,1180,"FDCP","FDCP11801HLX",null,"FDCP5601HLX     ","FDCP6151HLX     ",null,null,"その他",{"$f":"O381+O382","v":45.599999999999994},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,{"$f":"AN392*AO392","v":0},null,0,0,0,{"$error":"#N/A"},45.599999999999994,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,1235,"FDCP","FDCP12351HLX",null,"FDCP6151HLX     ","FDCP6151HLX     ",null,null,"その他",{"$f":"O382+O382","v":52.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},52.4,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,1300,"FDCP","FDCP13001HLX",null,"FDCP6151HLX     ","FDCP6801HLX     ",null,null,"その他",{"$f":"O382+O383","v":52.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},52.4,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,1360,"FDCP","FDCP13601HLX",null,"FDCP6801HLX     ","FDCP6801HLX     ",null,null,"その他",{"$f":"O383+O383","v":52.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},52.4,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,140,"FDCSP","FDCSP1401HLX    "," ",null,null,null,null,"その他",8.5,null,null,"",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,{"$f":"AR396","v":0},0,{"$error":"#N/A"},8.5,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,160,"FDCSP","FDCSP1601HLX    "," ",null,null,null,null,"その他",8.5,null,null,"",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,{"$f":"AR397","v":0},0,{"$error":"#N/A"},8.5,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,224,"FDCSP","FDCSP2241HLX    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,{"$f":"IF(B398=\"R410A\",0.42,IF(B398=\"R407C\",0.49,IF(B398=\"R22\",0.5,\"NG\")))","v":0.42},""]
[null,"R410A",1,null,null,280,"FDCSP","FDCSP2801HLX    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,335,"FDCSP","FDCSP3351HLX    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,335,"FDCSP","FDCSP3351HLX-K  "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,400,"FDCSP","FDCSP4001HLX    "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,450,"FDCSP","FDCSP4501HLX    "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,504,"FDCSP","FDCSP5041HLX    "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,560,"FDCSP","FDCSP5601HLX    "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,615,"FDCSP","FDCSP6151HLX    "," ",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,680,"FDCSP","FDCSP6801HLX    "," ",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,224,"FDCRP","FDCRP2241HLX    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,280,"FDCRP","FDCRP2801HLX    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,280,"FDCRP","FDCRP2801HLX-K  "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,335,"FDCRP","FDCRP3351HLX    "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,400,"FDCRP","FDCRP4001HLX    "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,450,"FDCRP","FDCRP4501HLX    "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,504,"FDCRP","FDCRP5041HLX    "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,560,"FDCRP","FDCRP5601HLX    "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,{"$f":"AR415","v":0},0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,615,"FDCRP","FDCRP6151HLX     ",null,"FDCRP2801HLX-K  ","FDCRP3351HLX    ",null,null,"その他",{"$f":"O410+O411","v":31.2},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,{"$f":"AR416","v":0},0,{"$error":"#N/A"},31.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,680,"FDCRP","FDCRP6801HLX     ",null,"FDCRP3351HLX    ","FDCRP3351HLX    ",null,null,"その他",{"$f":"O411+O411","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,735,"FDCRP","FDCRP7351HLX",null,"FDCRP3351HLX    ","FDCRP4001HLX    ",null,null,"その他",{"$f":"O411+O412","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,800,"FDCRP","FDCRP8001HLX",null,"FDCRP4001HLX    ","FDCRP4001HLX    ",null,null,"その他",{"$f":"O412+O412","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,850,"FDCRP","FDCRP8501HLX",null,"FDCRP4001HLX    ","FDCRP4501HLX    ",null,null,"その他",{"$f":"O412+O413","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,900,"FDCRP","FDCRP9001HLX",null,"FDCRP4501HLX    ","FDCRP4501HLX    ",null,null,"その他",{"$f":"O413+O413","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,960,"FDCRP","FDCRP9601HLX",null,"FDCRP4501HLX    ","FDCRP5041HLX    ",null,null,"その他",{"$f":"O413+O414","v":36.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},36.4,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,1010,"FDCRP","FDCRP10101HLX",null,"FDCRP5041HLX    ","FDCRP5041HLX    ",null,null,"その他",{"$f":"O414+O414","v":38.799999999999997},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},38.799999999999997,"",{"$f":"IF(B423=\"R410A\",0.39,IF(B423=\"R407C\",0.27,IF(B423=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(B423=\"R410A\",0.42,IF(B423=\"R407C\",0.46,IF(B423=\"R22\",0.28,\"NG\")))","v":0.42},0.42,""]
[null,"R410A",1,null,null,224,"FDCRSP","FDCRSP2241HLX   "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,280,"FDCRSP","FDCRSP2801HLX   "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,280,"FDCRSP","FDCRSP2801HLX-K "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,335,"FDCRSP","FDCRSP3351HLX   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,400,"FDCRSP","FDCRSP4001HLX   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,450,"FDCRSP","FDCRSP4501HLX   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,504,"FDCRSP","FDCRSP5041HLX   "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,560,"FDCRSP","FDCRSP5601HLX   "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",224,"FDCP","FDCP2241HLXR    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",280,"FDCP","FDCP2801HLXR    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",335,"FDCP","FDCP3351HLXR    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",335,"FDCP","FDCP3351HLXR-K  "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",400,"FDCP","FDCP4001HLXR    "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",450,"FDCP","FDCP4501HLXR    "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",504,"FDCP","FDCP5041HLXR    "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",560,"FDCP","FDCP5601HLXR    "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",615,"FDCP","FDCP6151HLXR    "," ",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",680,"FDCP","FDCP6801HLXR    "," ",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",735,"FDCP","FDCP7351HLXR",null,"FDCP3351HLXR-K  ","FDCP4001HLXR    ",null,null,"その他",{"$f":"O435+O436","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",800,"FDCP","FDCP8001HLXR",null,"FDCP4001HLXR    ","FDCP4001HLXR    ",null,null,"その他",{"$f":"O436+O436","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",850,"FDCP","FDCP8501HLXR",null,"FDCP4001HLXR    ","FDCP4501HLXR    ",null,null,"その他",{"$f":"O436+O437","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",900,"FDCP","FDCP9001HLXR",null,"FDCP4501HLXR    ","FDCP4501HLXR    ",null,null,"その他",{"$f":"O437+O437","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",960,"FDCP","FDCP9601HLXR",null,"FDCP4501HLXR    ","FDCP5041HLXR    ",null,null,"その他",{"$f":"O437+O438","v":36.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},36.4,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",1010,"FDCP","FDCP10101HLXR",null,"FDCP5041HLXR    ","FDCP5041HLXR    ",null,null,"その他",{"$f":"O438+O438","v":38.799999999999997},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},38.799999999999997,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",1065,"FDCP","FDCP10651HLXR",null,"FDCP5041HLXR    ","FDCP5601HLXR    ",null,null,"その他",{"$f":"O438+O439","v":38.799999999999997},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},38.799999999999997,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",1130,"FDCP","FDCP11301HLXR",null,"FDCP5601HLXR    ","FDCP5601HLXR    ",null,null,"その他",{"$f":"O439+O439","v":38.799999999999997},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},38.799999999999997,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",1180,"FDCP","FDCP11801HLXR",null,"FDCP5601HLXR    ","FDCP6151HLXR    ",null,null,"その他",{"$f":"O439+O440","v":45.599999999999994},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},45.599999999999994,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",1235,"FDCP","FDCP12351HLXR",null,"FDCP6151HLXR    ","FDCP6151HLXR    ",null,null,"その他",{"$f":"O440+O440","v":52.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},52.4,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",1300,"FDCP","FDCP13001HLXR",null,"FDCP6151HLXR    ","FDCP6801HLXR    ",null,null,"その他",{"$f":"O440+O441","v":52.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},52.4,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",1360,"FDCP","FDCP13601HLXR",null,"FDCP6801HLXR    ","FDCP6801HLXR    ",null,null,"その他",{"$f":"O441+O441","v":52.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},52.4,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",224,"FDCSP","FDCSP2241HLXR   "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",280,"FDCSP","FDCSP2801HLXR   "," ",null,null,null,null,"その他",14.2,null,null,{"$f":"IF(Q455=\"\",\"\",IF(Q455=\"90m未満\",VLOOKUP(C455&D455&\",\"&F455,主管サイズルックアップ用,5,FALSE),VLOOKUP(C455&D455&\",\"&F455,主管サイズルックアップ用,6,FALSE)))","v":""},null,2.1999999999999999E-2,{"$f":"IF($R455=\"***\",\"実長90m超使用不可\",IF($R455<6.35,\"-主管サイズを超過-\",IF(T455=\"***\",\"0\",S455*T455)))","v":0},null,5.3999999999999999E-2,{"$f":"IF($R455=\"***\",\"実長90m超使用不可\",IF($R455<9.52,\"-主管サイズを超過-\",IF(W455=\"***\",\"0\",V455*W455)))","v":0},null,0.11,{"$f":"IF($R455=\"***\",\"実長90m超使用不可\",IF($R455<12.7,\"-主管サイズを超過-\",IF(Z455=\"***\",\"0\",Y455*Z455)))","v":0},null,0.17,{"$f":"IF($R455=\"***\",\"実長90m超使用不可\",IF($R455<15.88,\"-主管サイズを超過-\",IF(AC455=\"***\",\"0\",AB455*AC455)))","v":0},null,0.25,{"$f":"IF($R455=\"***\",\"実長90m超使用不可\",IF($R455<19.05,\"-主管サイズを超過-\",IF(AF455=\"***\",\"0\",AE455*AF455)))","v":0},null,0.35,{"$f":"IF($R455=\"***\",\"実長90m超使用不可\",IF($R455<22.22,\"-主管サイズを超過-\",IF(AI455=\"***\",\"0\",AH455*AI455)))","v":0},null,"***",{"$f":"IF($R455=\"***\",\"実長90m超使用不可\",IF($R455<25.4,\"-主管サイズを超過-\",IF(AL455=\"***\",\"0\",AK455*AL455)))","v":"0"},{"$f":"IF(OR(U455=\"実長90m超使用不可\",U455=\"-主管サイズを超過-\"),0,U455)+IF(OR(X455=\"実長90m超使用不可\",X455=\"-主管サイズを超過-\"),0,X455)+IF(OR(AA455=\"実長90m超使用不可\",AA455=\"-主管サイズを超過-\"),0,AA455)+IF(OR(AD455=\"実長90m超使用不可\",AD455=\"-主管サイズを超過-\"),0,AD455)+IF(OR(AG455=\"実長90m超使用不可\",AG455=\"-主管サイズを超過-\"),0,AG455)+IF(OR(AJ455=\"実長90m超使用不可\",AJ455=\"-主管サイズを超過-\"),0,AJ455)+IF(OR(AM455=\"実長90m超使用不可\",AM455=\"-主管サイズを超過-\"),0,AM455)","v":0},1.3,0,null,0,0,{"$f":"IF(AP455+AS455<0,0,AP455+AS455)","v":0},{"$f":"VLOOKUP(C455&D455&\",\"&F455,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},{"$f":"O455+AT455","v":14.2},{"$f":"IF(ISERROR(AV455/P455),\"\",AV455/P455)","v":""},0.39,0.42,0.42,{"$f":"IF(AW455=\"\",\"\",IF(OR(AW455<=AX455,AND(N455=\"その他\",AW455<=AY455)),\"OK\",IF(OR(AND(N455=\"最下層\",AW455<=AY455),AND(N455=\"その他\",AW455<=AZ455)),\"対策が１つ必要です\",IF(OR(AND(N455=\"最下層\",AW455<=AZ455),AND(N455=\"その他\",AW455>AZ455)),\"対策が２つ必要です\",\"システムの見直しが必要です\"))))","v":""}]
[null,"R410A",1,null,"冷暖フリー",335,"FDCSP","FDCSP3351HLXR   "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,{"$f":"AN456*AO456","v":0},null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",335,"FDCSP","FDCSP3351HLXR-K "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",400,"FDCSP","FDCSP4001HLXR   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",450,"FDCSP","FDCSP4501HLXR   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",504,"FDCSP","FDCSP5041HLXR   "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",560,"FDCSP","FDCSP5601HLXR   "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",615,"FDCSP","FDCSP6151HLXR   "," ",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,"冷暖フリー",680,"FDCSP","FDCSP6801HLXR   "," ",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,224,"FDCP","FDCP2241HLX     ","A",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,280,"FDCP","FDCP2801HLX     ","A",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,335,"FDCP","FDCP3351HLX     ","A",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,450,"FDCP","FDCP4501HLX     ","A",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,504,"FDCP","FDCP5041HLX     ","A",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,560,"FDCP","FDCP5601HLX     ","A",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,615,"FDCP","FDCP6151HLX     ","A",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,680,"FDCP","FDCP6801HLX     ","A",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,224,"FDCSP","FDCSP2241HLX    ","A",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,280,"FDCSP","FDCSP2801HLX    ","A",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,335,"FDCSP","FDCSP3351HLX    ","A",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,450,"FDCSP","FDCSP4501HLX    ","A",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,504,"FDCSP","FDCSP5041HLX    ","A",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,560,"FDCSP","FDCSP5601HLX    ","A",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,615,"FDCSP","FDCSP6151HLX    ","A",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,680,"FDCSP","FDCSP6801HLX    ","A",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,280,"FDCP","FDCP2801HLXI    "," ","ISUP5601HLX","FDCP2801HLXI    ",null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,3,{"$f":"AR480","v":3},3,{"$error":"#N/A"},17.2,"",0.39,0.42,{"$f":"IF(B480=\"R410A\",0.42,IF(B480=\"R407C\",0.49,IF(B480=\"R22\",0.5,\"NG\")))","v":0.42},""]
[null,"R410A",1,null,null,335,"FDCP","FDCP3351HLXI    "," ","ISUP5601HLX","FDCP3351HLXI    ",null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,2,2,2,{"$error":"#N/A"},16.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,450,"FDCP","FDCP4501HLXI    "," ","ISUP5601HLX","FDCP4501HLXI    ",null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,2,2,2,{"$error":"#N/A"},19,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,280,"FDCSP","FDCSP2801HLXI   "," ","ISUSP5601HLX","FDCSP2801HLXI   ",null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,3,3,3,{"$error":"#N/A"},17.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,335,"FDCSP","FDCSP3351HLXI   "," ","ISUSP5601HLX","FDCSP3351HLXI   ",null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,2,2,2,{"$error":"#N/A"},16.2,"",0.39,0.42,0.42,""]
[null,"R410A",1,null,null,450,"FDCSP","FDCSP4501HLXI   "," ","ISUSP5601HLX","FDCSP4501HLXI   ",null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,2,2,2,{"$error":"#N/A"},19,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,140,"FDCP","FDCP1402HLX     "," ",null,null,null,null,"その他",7.5,null,null,"",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},7.5,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,160,"FDCP","FDCP1602HLX     "," ",null,null,null,null,"その他",7.5,null,null,"",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},7.5,"",{"$f":"IF(B487=\"R410A\",0.39,IF(B487=\"R407C\",0.27,IF(B487=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(B487=\"R410A\",0.42,IF(B487=\"R407C\",0.46,IF(B487=\"R22\",0.28,\"NG\")))","v":0.42},0.42,""]
[null,"R410A",2,null,null,224,"FDCP","FDCP2242HLX     "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCP","FDCP2802HLX     "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCP","FDCP3352HLX     "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCP","FDCP3352HLX-K   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,400,"FDCP","FDCP4002HLX     "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,450,"FDCP","FDCP4502HLX     "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,504,"FDCP","FDCP5042HLX     "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,560,"FDCP","FDCP5602HLX     "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,615,"FDCP","FDCP6152HLX     "," ",null,null,null,null,"その他",21.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},21.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,680,"FDCP","FDCP6802HLX     "," ",null,null,null,null,"その他",21.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},21.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,735,"FDCP","FDCP7352HLX",null,"FDCP3352HLX-K   ","FDCP4002HLX     ",null,null,"その他",{"$f":"O491+O492","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,800,"FDCP","FDCP8002HLX",null,"FDCP4002HLX     ","FDCP4002HLX     ",null,null,"その他",{"$f":"O492+O492","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,850,"FDCP","FDCP8502HLX",null,"FDCP4002HLX     ","FDCP4502HLX     ",null,null,"その他",{"$f":"O492+O493","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,900,"FDCP","FDCP9002HLX",null,"FDCP4502HLX     ","FDCP4502HLX     ",null,null,"その他",{"$f":"O493+O493","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,960,"FDCP","FDCP9602HLX",null,"FDCP4502HLX     ","FDCP5042HLX     ",null,null,"その他",{"$f":"O493+O494","v":36.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},36.4,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,1010,"FDCP","FDCP10102HLX",null,"FDCP5042HLX     ","FDCP5042HLX     ",null,null,"その他",{"$f":"O494+O494","v":38.799999999999997},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},38.799999999999997,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,1065,"FDCP","FDCP10652HLX",null,"FDCP5042HLX     ","FDCP5602HLX     ",null,null,"その他",{"$f":"O494+O495","v":38.799999999999997},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},38.799999999999997,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,1130,"FDCP","FDCP11302HLX",null,"FDCP5602HLX     ","FDCP5602HLX     ",null,null,"その他",{"$f":"O495+O495","v":38.799999999999997},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},38.799999999999997,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,1180,"FDCP","FDCP11802HLX",null,"FDCP5602HLX     ","FDCP6152HLX     ",null,null,"その他",{"$f":"O495+O496","v":40.599999999999994},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},40.599999999999994,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,1235,"FDCP","FDCP12352HLX",null,"FDCP6152HLX     ","FDCP6152HLX     ",null,null,"その他",{"$f":"O496+O496","v":42.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},42.4,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,1300,"FDCP","FDCP13002HLX",null,"FDCP6152HLX     ","FDCP6802HLX     ",null,null,"その他",{"$f":"O496+O497","v":42.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},42.4,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,1360,"FDCP","FDCP13602HLX",null,"FDCP6802HLX     ","FDCP6802HLX     ",null,null,"その他",{"$f":"O497+O497","v":42.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},42.4,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,140,"FDCSP","FDCSP1402HLX    "," ",null,null,null,null,"その他",7.5,null,null,"",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},7.5,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,160,"FDCSP","FDCSP1602HLX    "," ",null,null,null,null,"その他",7.5,null,null,"",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},7.5,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,224,"FDCSP","FDCSP2242HLX    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCSP","FDCSP2802HLX    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCSP","FDCSP3352HLX    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCSP","FDCSP3352HLX-K  "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,400,"FDCSP","FDCSP4002HLX    "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,450,"FDCSP","FDCSP4502HLX    "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,504,"FDCSP","FDCSP5042HLX    "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,560,"FDCSP","FDCSP5602HLX    "," ",null,null,null,null,"その他",19.399999999999999,null,null,{"$f":"IF(Q519=\"\",\"\",IF(Q519=\"90m未満\",VLOOKUP(C519&D519&\",\"&F519,主管サイズルックアップ用,5,FALSE),VLOOKUP(C519&D519&\",\"&F519,主管サイズルックアップ用,6,FALSE)))","v":""},null,2.1999999999999999E-2,{"$f":"IF($R519=\"***\",\"実長90m超使用不可\",IF($R519<6.35,\"-主管サイズを超過-\",IF(T519=\"***\",\"0\",S519*T519)))","v":0},null,5.3999999999999999E-2,{"$f":"IF($R519=\"***\",\"実長90m超使用不可\",IF($R519<9.52,\"-主管サイズを超過-\",IF(W519=\"***\",\"0\",V519*W519)))","v":0},null,0.11,{"$f":"IF($R519=\"***\",\"実長90m超使用不可\",IF($R519<12.7,\"-主管サイズを超過-\",IF(Z519=\"***\",\"0\",Y519*Z519)))","v":0},null,0.17,{"$f":"IF($R519=\"***\",\"実長90m超使用不可\",IF($R519<15.88,\"-主管サイズを超過-\",IF(AC519=\"***\",\"0\",AB519*AC519)))","v":0},null,0.25,{"$f":"IF($R519=\"***\",\"実長90m超使用不可\",IF($R519<19.05,\"-主管サイズを超過-\",IF(AF519=\"***\",\"0\",AE519*AF519)))","v":0},null,0.35,{"$f":"IF($R519=\"***\",\"実長90m超使用不可\",IF($R519<22.22,\"-主管サイズを超過-\",IF(AI519=\"***\",\"0\",AH519*AI519)))","v":0},null,"***",{"$f":"IF($R519=\"***\",\"実長90m超使用不可\",IF($R519<25.4,\"-主管サイズを超過-\",IF(AL519=\"***\",\"0\",AK519*AL519)))","v":"0"},{"$f":"IF(OR(U519=\"実長90m超使用不可\",U519=\"-主管サイズを超過-\"),0,U519)+IF(OR(X519=\"実長90m超使用不可\",X519=\"-主管サイズを超過-\"),0,X519)+IF(OR(AA519=\"実長90m超使用不可\",AA519=\"-主管サイズを超過-\"),0,AA519)+IF(OR(AD519=\"実長90m超使用不可\",AD519=\"-主管サイズを超過-\"),0,AD519)+IF(OR(AG519=\"実長90m超使用不可\",AG519=\"-主管サイズを超過-\"),0,AG519)+IF(OR(AJ519=\"実長90m超使用不可\",AJ519=\"-主管サイズを超過-\"),0,AJ519)+IF(OR(AM519=\"実長90m超使用不可\",AM519=\"-主管サイズを超過-\"),0,AM519)","v":0},null,0,null,0,0,{"$f":"IF(AP519+AS519<0,0,AP519+AS519)","v":0},{"$f":"VLOOKUP(C519&D519&\",\"&F519,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},{"$f":"O519+AT519","v":19.399999999999999},{"$f":"IF(ISERROR(AV519/P519),\"\",AV519/P519)","v":""},0.39,0.42,0.42,{"$f":"IF(AW519=\"\",\"\",IF(OR(AW519<=AX519,AND(N519=\"その他\",AW519<=AY519)),\"OK\",IF(OR(AND(N519=\"最下層\",AW519<=AY519),AND(N519=\"その他\",AW519<=AZ519)),\"対策が１つ必要です\",IF(OR(AND(N519=\"最下層\",AW519<=AZ519),AND(N519=\"その他\",AW519>AZ519)),\"対策が２つ必要です\",\"システムの見直しが必要です\"))))","v":""}]
[null,"R410A",2,null,null,615,"FDCSP","FDCSP6152HLX    "," ",null,null,null,null,"その他",21.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,{"$f":"AN520*AO520","v":0},null,0,0,0,{"$error":"#N/A"},21.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,680,"FDCSP","FDCSP6802HLX    "," ",null,null,null,null,"その他",21.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},21.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",224,"FDCP","FDCP2242HLXR    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",280,"FDCP","FDCP2802HLXR    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",335,"FDCP","FDCP3352HLXR    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",335,"FDCP","FDCP3352HLXR-K  "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",400,"FDCP","FDCP4002HLXR    "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",450,"FDCP","FDCP4502HLXR    "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",504,"FDCP","FDCP5042HLXR    "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",560,"FDCP","FDCP5602HLXR    "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",615,"FDCP","FDCP6152HLXR    "," ",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",680,"FDCP","FDCP6802HLXR    "," ",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",735,"FDCP","FDCP7352HLXR",null,"FDCP3352HLXR-K   ","FDCP4002HLXR     ",null,null,"その他",{"$f":"O525+O526","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",800,"FDCP","FDCP8002HLXR",null,"FDCP4002HLXR   ","FDCP4002HLXR     ",null,null,"その他",{"$f":"O526+O526","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",850,"FDCP","FDCP8502HLXR",null,"FDCP4002HLXR     ","FDCP4502HLXR     ",null,null,"その他",{"$f":"O526+O527","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",900,"FDCP","FDCP9002HLXR",null,"FDCP4502HLXR     ","FDCP4502HLXR     ",null,null,"その他",{"$f":"O527+O527","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",960,"FDCP","FDCP9602HLXR",null,"FDCP4502HLXR     ","FDCP5042HLXR     ",null,null,"その他",{"$f":"O527+O528","v":36.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},36.4,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",1010,"FDCP","FDCP10102HLXR",null,"FDCP5042HLXR     ","FDCP5042HLXR     ",null,null,"その他",{"$f":"O528+O528","v":38.799999999999997},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},38.799999999999997,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",1065,"FDCP","FDCP10652HLXR",null,"FDCP5042HLXR     ","FDCP5602HLXR     ",null,null,"その他",{"$f":"O528+O529","v":38.799999999999997},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},38.799999999999997,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",1130,"FDCP","FDCP11302HLXR",null,"FDCP5602HLXR     ","FDCP5602HLXR     ",null,null,"その他",{"$f":"O529+O529","v":38.799999999999997},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},38.799999999999997,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",1180,"FDCP","FDCP11802HLXR",null,"FDCP5602HLXR     ","FDCP6152HLXR     ",null,null,"その他",{"$f":"O529+O530","v":45.599999999999994},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},45.599999999999994,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",1235,"FDCP","FDCP12352HLXR",null,"FDCP6152HLXR     ","FDCP6152HLXR     ",null,null,"その他",{"$f":"O530+O530","v":52.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},52.4,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",1300,"FDCP","FDCP13002HLXR",null,"FDCP6152HLXR     ","FDCP6802HLXR     ",null,null,"その他",{"$f":"O530+O531","v":52.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},52.4,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",1360,"FDCP","FDCP13602HLXR",null,"FDCP6802HLXR     ","FDCP6802HLXR     ",null,null,"その他",{"$f":"O531+O531","v":52.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},52.4,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",224,"FDCSP","FDCSP2242HLXR   "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,{"$f":"AR544","v":0},0,{"$error":"#N/A"},14.2,"",0.39,0.42,{"$f":"IF(B544=\"R410A\",0.42,IF(B544=\"R407C\",0.49,IF(B544=\"R22\",0.5,\"NG\")))","v":0.42},""]
[null,"R410A",2,null,"冷暖フリー",280,"FDCSP","FDCSP2802HLXR   "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",335,"FDCSP","FDCSP3352HLXR   "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",335,"FDCSP","FDCSP3352HLXR-K "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",400,"FDCSP","FDCSP4002HLXR   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",450,"FDCSP","FDCSP4502HLXR   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",504,"FDCSP","FDCSP5042HLXR   "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",560,"FDCSP","FDCSP5602HLXR   "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",{"$f":"IF(B551=\"R410A\",0.39,IF(B551=\"R407C\",0.27,IF(B551=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(B551=\"R410A\",0.42,IF(B551=\"R407C\",0.46,IF(B551=\"R22\",0.28,\"NG\")))","v":0.42},0.42,""]
[null,"R410A",2,null,"冷暖フリー",615,"FDCSP","FDCSP6152HLXR   "," ",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",680,"FDCSP","FDCSP6802HLXR   "," ",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,224,"FDCRP","FDCRP2242HLX    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCRP","FDCRP2802HLX    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCRP","FDCRP2802HLX-K  "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCRP","FDCRP3352HLX    "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,400,"FDCRP","FDCRP4002HLX    "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,450,"FDCRP","FDCRP4502HLX    "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,504,"FDCRP","FDCRP5042HLX    "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,560,"FDCRP","FDCRP5602HLX    "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,615,"FDCRP","FDCRP6152HLX     ",null,"FDCRP2802HLX-K  ","FDCRP3352HLX    ",null,null,"その他",{"$f":"O556+O557","v":31.2},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},31.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,680,"FDCRP","FDCRP6802HLX     ",null,"FDCRP3352HLX    ","FDCRP3352HLX    ",null,null,"その他",{"$f":"O557+O557","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,735,"FDCRP","FDCRP7352HLX",null,"FDCRP3352HLX    ","FDCRP4002HLX    ",null,null,"その他",{"$f":"O557+O558","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,800,"FDCRP","FDCRP8002HLX",null,"FDCRP4002HLX    ","FDCRP4002HLX    ",null,null,"その他",{"$f":"O558+O558","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,850,"FDCRP","FDCRP8502HLX",null,"FDCRP4002HLX    ","FDCRP4502HLX    ",null,null,"その他",{"$f":"O558+O559","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,900,"FDCRP","FDCRP9002HLX",null,"FDCRP4502HLX    ","FDCRP4502HLX    ",null,null,"その他",{"$f":"O559+O559","v":34},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},34,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,960,"FDCRP","FDCRP9602HLX",null,"FDCRP4502HLX    ","FDCRP5042HLX    ",null,null,"その他",{"$f":"O559+O560","v":36.4},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},36.4,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,1010,"FDCRP","FDCRP10102HLX",null,"FDCRP5042HLX    ","FDCRP5042HLX    ",null,null,"その他",{"$f":"O560+O560","v":38.799999999999997},null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},38.799999999999997,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,224,"FDCRSP","FDCRSP2242HLX   "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCRSP","FDCRSP2802HLX   "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCRSP","FDCRSP2802HLX-K "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCRSP","FDCRSP3352HLX   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,400,"FDCRSP","FDCRSP4002HLX   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,450,"FDCRSP","FDCRSP4502HLX   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,504,"FDCRSP","FDCRSP5042HLX   "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,560,"FDCRSP","FDCRSP5602HLX   "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCP","FDCP2802HLXI    "," ","ISUP5602HLX","FDCP2802HLXI    ",null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,3,3,3,{"$error":"#N/A"},17.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCP","FDCP3352HLXI    "," ","ISUP5602HLX","FDCP3352HLXI    ",null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,2,2,2,{"$error":"#N/A"},16.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,450,"FDCP","FDCP4502HLXI    "," ","ISUP5602HLX","FDCP4502HLXI    ",null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,2,2,2,{"$error":"#N/A"},19,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCSP","FDCSP2802HLXI   "," ","ISUSP5602HLX","FDCSP2802HLXI   ",null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,3,3,3,{"$error":"#N/A"},17.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCSP","FDCSP3352HLXI   "," ","ISUSP5602HLX","FDCSP3352HLXI   ",null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,2,2,2,{"$error":"#N/A"},16.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,450,"FDCSP","FDCSP4502HLXI   "," ","ISUSP5602HLX","FDCSP4502HLXI   ",null,null,"その他",17,null,null,{"$f":"IF(Q583=\"\",\"\",IF(Q583=\"90m未満\",VLOOKUP(C583&D583&\",\"&F583,主管サイズルックアップ用,5,FALSE),VLOOKUP(C583&D583&\",\"&F583,主管サイズルックアップ用,6,FALSE)))","v":""},null,2.1999999999999999E-2,{"$f":"IF($R583=\"***\",\"実長90m超使用不可\",IF($R583<6.35,\"-主管サイズを超過-\",IF(T583=\"***\",\"0\",S583*T583)))","v":0},null,5.3999999999999999E-2,{"$f":"IF($R583=\"***\",\"実長90m超使用不可\",IF($R583<9.52,\"-主管サイズを超過-\",IF(W583=\"***\",\"0\",V583*W583)))","v":0},null,0.11,{"$f":"IF($R583=\"***\",\"実長90m超使用不可\",IF($R583<12.7,\"-主管サイズを超過-\",IF(Z583=\"***\",\"0\",Y583*Z583)))","v":0},null,0.17,{"$f":"IF($R583=\"***\",\"実長90m超使用不可\",IF($R583<15.88,\"-主管サイズを超過-\",IF(AC583=\"***\",\"0\",AB583*AC583)))","v":0},null,0.25,{"$f":"IF($R583=\"***\",\"実長90m超使用不可\",IF($R583<19.05,\"-主管サイズを超過-\",IF(AF583=\"***\",\"0\",AE583*AF583)))","v":0},null,0.35,{"$f":"IF($R583=\"***\",\"実長90m超使用不可\",IF($R583<22.22,\"-主管サイズを超過-\",IF(AI583=\"***\",\"0\",AH583*AI583)))","v":0},null,"***",{"$f":"IF($R583=\"***\",\"実長90m超使用不可\",IF($R583<25.4,\"-主管サイズを超過-\",IF(AL583=\"***\",\"0\",AK583*AL583)))","v":"0"},{"$f":"IF(OR(U583=\"実長90m超使用不可\",U583=\"-主管サイズを超過-\"),0,U583)+IF(OR(X583=\"実長90m超使用不可\",X583=\"-主管サイズを超過-\"),0,X583)+IF(OR(AA583=\"実長90m超使用不可\",AA583=\"-主管サイズを超過-\"),0,AA583)+IF(OR(AD583=\"実長90m超使用不可\",AD583=\"-主管サイズを超過-\"),0,AD583)+IF(OR(AG583=\"実長90m超使用不可\",AG583=\"-主管サイズを超過-\"),0,AG583)+IF(OR(AJ583=\"実長90m超使用不可\",AJ583=\"-主管サイズを超過-\"),0,AJ583)+IF(OR(AM583=\"実長90m超使用不可\",AM583=\"-主管サイズを超過-\"),0,AM583)","v":0},null,0,null,2,2,{"$f":"IF(AP583+AS583<0,0,AP583+AS583)","v":2},{"$f":"VLOOKUP(C583&D583&\",\"&F583,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},{"$f":"O583+AT583","v":19},{"$f":"IF(ISERROR(AV583/P583),\"\",AV583/P583)","v":""},0.39,0.42,0.42,{"$f":"IF(AW583=\"\",\"\",IF(OR(AW583<=AX583,AND(N583=\"その他\",AW583<=AY583)),\"OK\",IF(OR(AND(N583=\"最下層\",AW583<=AY583),AND(N583=\"その他\",AW583<=AZ583)),\"対策が１つ必要です\",IF(OR(AND(N583=\"最下層\",AW583<=AZ583),AND(N583=\"その他\",AW583>AZ583)),\"対策が２つ必要です\",\"システムの見直しが必要です\"))))","v":""}]
[null,"R410A",2,null,null,140,"FDCP","FDCP1402HLXB    "," ",null,null,null,null,"その他",7.5,null,null,"",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,{"$f":"AN584*AO584","v":0},null,0,0,0,{"$error":"#N/A"},7.5,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,160,"FDCP","FDCP1602HLXB    "," ",null,null,null,null,"その他",7.5,null,null,"",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},7.5,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,224,"FDCP","FDCP2242HLXB    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCP","FDCP2802HLXB    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCP","FDCP3352HLXB    "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCP","FDCP3352HLXB-K  "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,400,"FDCP","FDCP4002HLXB    "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,450,"FDCP","FDCP4502HLXB    "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,504,"FDCP","FDCP5042HLXB    "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,560,"FDCP","FDCP5602HLXB    "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,615,"FDCP","FDCP6152HLXB    "," ",null,null,null,null,"その他",21.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},21.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,680,"FDCP","FDCP6802HLXB    "," ",null,null,null,null,"その他",21.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},21.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCP","FDCP2802HLXIB   "," ","ISUP5602HLX","FDCP2802HLXIB   ",null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,3,3,3,{"$error":"#N/A"},17.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCP","FDCP3352HLXIB   "," ","ISUP5602HLX","FDCP3352HLXIB   ",null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,2,2,2,{"$error":"#N/A"},16.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,450,"FDCP","FDCP4502HLXIB   "," ","ISUP5602HLX","FDCP4502HLXIB   ",null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,2,2,2,{"$error":"#N/A"},19,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",224,"FDCP","FDCP2242HLXRB   "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",280,"FDCP","FDCP2802HLXRB   "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",335,"FDCP","FDCP3352HLXRB   "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",335,"FDCP","FDCP3352HLXRB-K "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",400,"FDCP","FDCP4002HLXRB   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",450,"FDCP","FDCP4502HLXRB   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",504,"FDCP","FDCP5042HLXRB   "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",560,"FDCP","FDCP5602HLXRB   "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",615,"FDCP","FDCP6152HLXRB   "," ",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,"冷暖フリー",680,"FDCP","FDCP6802HLXRB   "," ",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,{"$f":"AR608","v":0},0,{"$error":"#N/A"},26.2,"",0.39,0.42,{"$f":"IF(B608=\"R410A\",0.42,IF(B608=\"R407C\",0.49,IF(B608=\"R22\",0.5,\"NG\")))","v":0.42},""]
[null,"R410A",2,null,null,224,"FDCRP","FDCRP2242HLXB   "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCRP","FDCRP2802HLXB   "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCRP","FDCRP2802HLXB-K "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCRP","FDCRP3352HLXB   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,400,"FDCRP","FDCRP4002HLXB   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,450,"FDCRP","FDCRP4502HLXB   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,504,"FDCRP","FDCRP5042HLXB   "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",{"$f":"IF(B615=\"R410A\",0.39,IF(B615=\"R407C\",0.27,IF(B615=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(B615=\"R410A\",0.42,IF(B615=\"R407C\",0.46,IF(B615=\"R22\",0.28,\"NG\")))","v":0.42},0.42,""]
[null,"R410A",2,null,null,560,"FDCRP","FDCRP5602HLXB   "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,224,"FDCRSP","FDCRSP2242HLXB  "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCRSP","FDCRSP2802HLXB  "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCRSP","FDCRSP2802HLXB-K"," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCRSP","FDCRSP3352HLXB  "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,400,"FDCRSP","FDCRSP4002HLXB  "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,450,"FDCRSP","FDCRSP4502HLXB  "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,504,"FDCRSP","FDCRSP5042HLXB  "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,560,"FDCRSP","FDCRSP5602HLXB  "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,140,"FDCSP","FDCSP1402HLXB   "," ",null,null,null,null,"その他",7.5,null,null,"",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},7.5,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,160,"FDCSP","FDCSP1602HLXB   "," ",null,null,null,null,"その他",7.5,null,null,"",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},7.5,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,224,"FDCSP","FDCSP2242HLXB   "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCSP","FDCSP2802HLXB   "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCSP","FDCSP3352HLXB   "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCSP","FDCSP3352HLXB-K "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,400,"FDCSP","FDCSP4002HLXB   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,450,"FDCSP","FDCSP4502HLXB   "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,504,"FDCSP","FDCSP5042HLXB   "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,560,"FDCSP","FDCSP5602HLXB   "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,615,"FDCSP","FDCSP6152HLXB   "," ",null,null,null,null,"その他",21.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},21.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,680,"FDCSP","FDCSP6802HLXB   "," ",null,null,null,null,"その他",21.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},21.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCSP","FDCSP2802HLXIB  "," ","ISUSP5602HLX","FDCSP2802HLXIB  ",null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,3,3,3,{"$error":"#N/A"},17.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCSP","FDCSP3352HLXIB  "," ","ISUSP5602HLX","FDCSP3352HLXIB  ",null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,2,2,2,{"$error":"#N/A"},16.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,450,"FDCSP","FDCSP4502HLXIB  "," ","ISUSP5602HLX","FDCSP4502HLXIB  ",null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,2,2,2,{"$error":"#N/A"},19,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,224,"FDCSP","FDCSP2242HLXRB  "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCSP","FDCSP2802HLXRB  "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCSP","FDCSP3352HLXRB  "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCSP","FDCSP3352HLXRB-K"," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,400,"FDCSP","FDCSP4002HLXRB  "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,450,"FDCSP","FDCSP4502HLXRB  "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,504,"FDCSP","FDCSP5042HLXRB  "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,560,"FDCSP","FDCSP5602HLXRB  "," ",null,null,null,null,"その他",19.399999999999999,null,null,{"$f":"IF(Q647=\"\",\"\",IF(Q647=\"90m未満\",VLOOKUP(C647&D647&\",\"&F647,主管サイズルックアップ用,5,FALSE),VLOOKUP(C647&D647&\",\"&F647,主管サイズルックアップ用,6,FALSE)))","v":""},null,2.1999999999999999E-2,{"$f":"IF($R647=\"***\",\"実長90m超使用不可\",IF($R647<6.35,\"-主管サイズを超過-\",IF(T647=\"***\",\"0\",S647*T647)))","v":0},null,5.3999999999999999E-2,{"$f":"IF($R647=\"***\",\"実長90m超使用不可\",IF($R647<9.52,\"-主管サイズを超過-\",IF(W647=\"***\",\"0\",V647*W647)))","v":0},null,0.11,{"$f":"IF($R647=\"***\",\"実長90m超使用不可\",IF($R647<12.7,\"-主管サイズを超過-\",IF(Z647=\"***\",\"0\",Y647*Z647)))","v":0},null,0.17,{"$f":"IF($R647=\"***\",\"実長90m超使用不可\",IF($R647<15.88,\"-主管サイズを超過-\",IF(AC647=\"***\",\"0\",AB647*AC647)))","v":0},null,0.25,{"$f":"IF($R647=\"***\",\"実長90m超使用不可\",IF($R647<19.05,\"-主管サイズを超過-\",IF(AF647=\"***\",\"0\",AE647*AF647)))","v":0},null,0.35,{"$f":"IF($R647=\"***\",\"実長90m超使用不可\",IF($R647<22.22,\"-主管サイズを超過-\",IF(AI647=\"***\",\"0\",AH647*AI647)))","v":0},null,"***",{"$f":"IF($R647=\"***\",\"実長90m超使用不可\",IF($R647<25.4,\"-主管サイズを超過-\",IF(AL647=\"***\",\"0\",AK647*AL647)))","v":"0"},{"$f":"IF(OR(U647=\"実長90m超使用不可\",U647=\"-主管サイズを超過-\"),0,U647)+IF(OR(X647=\"実長90m超使用不可\",X647=\"-主管サイズを超過-\"),0,X647)+IF(OR(AA647=\"実長90m超使用不可\",AA647=\"-主管サイズを超過-\"),0,AA647)+IF(OR(AD647=\"実長90m超使用不可\",AD647=\"-主管サイズを超過-\"),0,AD647)+IF(OR(AG647=\"実長90m超使用不可\",AG647=\"-主管サイズを超過-\"),0,AG647)+IF(OR(AJ647=\"実長90m超使用不可\",AJ647=\"-主管サイズを超過-\"),0,AJ647)+IF(OR(AM647=\"実長90m超使用不可\",AM647=\"-主管サイズを超過-\"),0,AM647)","v":0},1.3,0,null,0,0,{"$f":"IF(AP647+AS647<0,0,AP647+AS647)","v":0},{"$f":"VLOOKUP(C647&D647&\",\"&F647,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},{"$f":"O647+AT647","v":19.399999999999999},{"$f":"IF(ISERROR(AV647/P647),\"\",AV647/P647)","v":""},0.39,0.42,0.42,{"$f":"IF(AW647=\"\",\"\",IF(OR(AW647<=AX647,AND(N647=\"その他\",AW647<=AY647)),\"OK\",IF(OR(AND(N647=\"最下層\",AW647<=AY647),AND(N647=\"その他\",AW647<=AZ647)),\"対策が１つ必要です\",IF(OR(AND(N647=\"最下層\",AW647<=AZ647),AND(N647=\"その他\",AW647>AZ647)),\"対策が２つ必要です\",\"システムの見直しが必要です\"))))","v":""}]
[null,"R410A",2,null,null,615,"FDCSP","FDCSP6152HLXRB  "," ",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,{"$f":"AN648*AO648","v":0},null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,680,"FDCSP","FDCSP6802HLXRB  "," ",null,null,null,null,"その他",26.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},26.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,224,"FDCP","FDCP2242HLXB-V  "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCP","FDCP2802HLXB-V  "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCP","FDCP3352HLXB-KV "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCP","FDCP3352HLXB-V  "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,400,"FDCP","FDCP4002HLXB-V  "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,450,"FDCP","FDCP4502HLXB-V  "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,504,"FDCP","FDCP5042HLXB-V  "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,560,"FDCP","FDCP5602HLXB-V  "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,615,"FDCP","FDCP6152HLXB-V  "," ",null,null,null,null,"その他",21.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},21.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,680,"FDCP","FDCP6802HLXB-V  "," ",null,null,null,null,"その他",21.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},21.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,224,"FDCSP","FDCSP2242HLXB-V "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,280,"FDCSP","FDCSP2802HLXB-V "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCSP","FDCSP3352HLXB-KV"," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,335,"FDCSP","FDCSP3352HLXB-V "," ",null,null,null,null,"その他",14.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},14.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,400,"FDCSP","FDCSP4002HLXB-V "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,450,"FDCSP","FDCSP4502HLXB-V "," ",null,null,null,null,"その他",17,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},17,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,504,"FDCSP","FDCSP5042HLXB-V "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,560,"FDCSP","FDCSP5602HLXB-V "," ",null,null,null,null,"その他",19.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},19.399999999999999,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,615,"FDCSP","FDCSP6152HLXB-V "," ",null,null,null,null,"その他",21.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},21.2,"",0.39,0.42,0.42,""]
[null,"R410A",2,null,null,680,"FDCSP","FDCSP6802HLXB-V "," ",null,null,null,null,"その他",21.2,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,0.25,0,null,0.35,0,null,"***","0",0,null,0,null,0,0,0,{"$error":"#N/A"},21.2,"",0.39,0.42,0.42,""]
[null,"R410A",3,null,null,112,"FDCP","FDCP1123HLX     "," ",null,null,null,null,"その他",5,null,"90m未満",9.52,10,2.1999999999999999E-2,{"$f":"IF($R670=\"***\",\"実長90m超使用不可\",IF($R670<6.35,\"-主管サイズを超過-\",IF(T670=\"***\",\"0\",S670*T670)))","v":0.21999999999999997},20,5.3999999999999999E-2,{"$f":"IF($R670=\"***\",\"実長90m超使用不可\",IF($R670<9.52,\"-主管サイズを超過-\",IF(W670=\"***\",\"0\",V670*W670)))","v":1.08},null,"***",{"$f":"IF($R670=\"***\",\"実長90m超使用不可\",IF($R670<12.7,\"-主管サイズを超過-\",IF(Z670=\"***\",\"0\",Y670*Z670)))","v":"-主管サイズを超過-"},null,"***",{"$f":"IF($R670=\"***\",\"実長90m超使用不可\",IF($R670<15.88,\"-主管サイズを超過-\",IF(AC670=\"***\",\"0\",AB670*AC670)))","v":"-主管サイズを超過-"},null,"***",{"$f":"IF($R670=\"***\",\"実長90m超使用不可\",IF($R670<19.05,\"-主管サイズを超過-\",IF(AF670=\"***\",\"0\",AE670*AF670)))","v":"-主管サイズを超過-"},null,"***",{"$f":"IF($R670=\"***\",\"実長90m超使用不可\",IF($R670<22.22,\"-主管サイズを超過-\",IF(AI670=\"***\",\"0\",AH670*AI670)))","v":"-主管サイズを超過-"},null,"***",{"$f":"IF($R670=\"***\",\"実長90m超使用不可\",IF($R670<25.4,\"-主管サイズを超過-\",IF(AL670=\"***\",\"0\",AK670*AL670)))","v":"-主管サイズを超過-"},{"$f":"IF(OR(U670=\"実長90m超使用不可\",U670=\"-主管サイズを超過-\"),0,U670)+IF(OR(X670=\"実長90m超使用不可\",X670=\"-主管サイズを超過-\"),0,X670)+IF(OR(AA670=\"実長90m超使用不可\",AA670=\"-主管サイズを超過-\"),0,AA670)+IF(OR(AD670=\"実長90m超使用不可\",AD670=\"-主管サイズを超過-\"),0,AD670)+IF(OR(AG670=\"実長90m超使用不可\",AG670=\"-主管サイズを超過-\"),0,AG670)+IF(OR(AJ670=\"実長90m超使用不可\",AJ670=\"-主管サイズを超過-\"),0,AJ670)+IF(OR(AM670=\"実長90m超使用不可\",AM670=\"-主管サイズを超過-\"),0,AM670)","v":1.3},null,0,null,{"$f":"3.38-O670","v":-1.62},{"$f":"AR670","v":-1.62},0,50,5,"",0.39,0.42,0.42,"",{"$f":"IF(AND(C670=3,AT670>AU670),\"追加封入量の上限を超えています\",\"\")","v":""}]
[null,"R410A",3,null,null,140,"FDCP","FDCP1403HLX     "," ",null,null,null,null,"その他",5,null,"90m以上","***",null,2.1999999999999999E-2,{"$f":"IF($R671=\"***\",\"実長90m超使用不可\",IF($R671<6.35,\"-主管サイズを超過-\",IF(T671=\"***\",\"0\",S671*T671)))","v":"実長90m超使用不可"},null,5.3999999999999999E-2,{"$f":"IF($R671=\"***\",\"実長90m超使用不可\",IF($R671<9.52,\"-主管サイズを超過-\",IF(W671=\"***\",\"0\",V671*W671)))","v":"実長90m超使用不可"},null,"***",{"$f":"IF($R671=\"***\",\"実長90m超使用不可\",IF($R671<12.7,\"-主管サイズを超過-\",IF(Z671=\"***\",\"0\",Y671*Z671)))","v":"実長90m超使用不可"},null,"***",{"$f":"IF($R671=\"***\",\"実長90m超使用不可\",IF($R671<15.88,\"-主管サイズを超過-\",IF(AC671=\"***\",\"0\",AB671*AC671)))","v":"実長90m超使用不可"},null,"***",{"$f":"IF($R671=\"***\",\"実長90m超使用不可\",IF($R671<19.05,\"-主管サイズを超過-\",IF(AF671=\"***\",\"0\",AE671*AF671)))","v":"実長90m超使用不可"},null,"***",{"$f":"IF($R671=\"***\",\"実長90m超使用不可\",IF($R671<22.22,\"-主管サイズを超過-\",IF(AI671=\"***\",\"0\",AH671*AI671)))","v":"実長90m超使用不可"},null,"***",{"$f":"IF($R671=\"***\",\"実長90m超使用不可\",IF($R671<25.4,\"-主管サイズを超過-\",IF(AL671=\"***\",\"0\",AK671*AL671)))","v":"実長90m超使用不可"},{"$f":"IF(OR(U671=\"実長90m超使用不可\",U671=\"-主管サイズを超過-\"),0,U671)+IF(OR(X671=\"実長90m超使用不可\",X671=\"-主管サイズを超過-\"),0,X671)+IF(OR(AA671=\"実長90m超使用不可\",AA671=\"-主管サイズを超過-\"),0,AA671)+IF(OR(AD671=\"実長90m超使用不可\",AD671=\"-主管サイズを超過-\"),0,AD671)+IF(OR(AG671=\"実長90m超使用不可\",AG671=\"-主管サイズを超過-\"),0,AG671)+IF(OR(AJ671=\"実長90m超使用不可\",AJ671=\"-主管サイズを超過-\"),0,AJ671)+IF(OR(AM671=\"実長90m超使用不可\",AM671=\"-主管サイズを超過-\"),0,AM671)","v":0},null,0,null,{"$f":"3.38-O671","v":-1.62},-1.62,0,50,5,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,112,"FDCSP","FDCSP1123HLX    "," ",null,null,null,null,"その他",5,null,"90m以上","***",null,2.1999999999999999E-2,"実長90m超使用不可",null,5.3999999999999999E-2,"実長90m超使用不可",null,"***","実長90m超使用不可",null,"***","実長90m超使用不可",null,"***","実長90m超使用不可",null,"***","実長90m超使用不可",null,"***","実長90m超使用不可",0,null,0,null,{"$f":"3.38-O672","v":-1.62},{"$f":"AR672","v":-1.62},0,50,5,"",0.39,0.42,{"$f":"IF(B672=\"R410A\",0.42,IF(B672=\"R407C\",0.49,IF(B672=\"R22\",0.5,\"NG\")))","v":0.42},"",""]
[null,"R410A",3,null,null,140,"FDCSP","FDCSP1403HLX    "," ",null,null,null,null,"その他",5,null,"90m未満",9.52,null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,"***","-主管サイズを超過-",null,"***","-主管サイズを超過-",null,"***","-主管サイズを超過-",null,"***","-主管サイズを超過-",null,"***","-主管サイズを超過-",0,null,0,null,{"$f":"3.38-O673","v":-1.62},-1.62,0,50,5,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,224,"FDCP","FDCP2243HLXY    "," ",null,null,null,null,"その他",14,null,"90m以上",12.7,null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,"-主管サイズを超過-",null,"***","-主管サイズを超過-",null,"***","-主管サイズを超過-",null,"***","-主管サイズを超過-",0,null,0,null,0,0,0,50,14,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,280,"FDCP","FDCP2803HLXY    "," ",null,null,null,null,"その他",14,null,"90m以上",12.7,null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,"-主管サイズを超過-",null,"***","-主管サイズを超過-",null,"***","-主管サイズを超過-",null,"***","-主管サイズを超過-",0,null,0,null,0,0,0,50,14,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,335,"FDCP","FDCP3353HLXY    "," ",null,null,null,null,"その他",14,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,50,14,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,224,"FDCSP","FDCSP2243HLXY   "," ",null,null,null,null,"その他",14,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,50,14,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,280,"FDCSP","FDCSP2803HLXY   "," ",null,null,null,null,"その他",14,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,50,14,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,335,"FDCSP","FDCSP3353HLXY   "," ",null,null,null,null,"その他",14,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,50,14,"",{"$f":"IF(B679=\"R410A\",0.39,IF(B679=\"R407C\",0.27,IF(B679=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(B679=\"R410A\",0.42,IF(B679=\"R407C\",0.46,IF(B679=\"R22\",0.28,\"NG\")))","v":0.42},0.42,"",""]
[null,"R410A",3,null,null,335,"FDCP","FDCP3353HLX-K   "," ",null,null,null,null,"その他",11.9,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,11.9,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,400,"FDCP","FDCP4003HLX     "," ",null,null,null,null,"その他",12.8,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,12.8,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,450,"FDCP","FDCP4503HLX     "," ",null,null,null,null,"その他",14.6,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,14.6,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,504,"FDCP","FDCP5043HLX     "," ",null,null,null,null,"その他",16.3,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,16.3,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,560,"FDCP","FDCP5603HLX     "," ",null,null,null,null,"その他",17.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,17.399999999999999,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,615,"FDCP","FDCP6153HLX     "," ",null,null,null,null,"その他",18.600000000000001,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,18.600000000000001,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,680,"FDCP","FDCP6803HLX     "," ",null,null,null,null,"その他",19.899999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,19.899999999999999,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,735,"FDCP","FDCP7353HLX     "," ","FDCP3353HLX-K   ","FDCP4003HLX     ",null,null,"その他",{"$f":"O680+O681","v":24.700000000000003},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,24.700000000000003,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,800,"FDCP","FDCP8003HLX     "," ","FDCP4003HLX     ","FDCP4003HLX     ",null,null,"その他",{"$f":"O681+O681","v":25.6},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,25.6,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,850,"FDCP","FDCP8503HLX     "," ","FDCP4003HLX     ","FDCP4503HLX     ",null,null,"その他",{"$f":"O681+O682","v":27.4},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,27.4,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,900,"FDCP","FDCP9003HLX     "," ","FDCP4503HLX     ","FDCP4503HLX     ",null,null,"その他",{"$f":"O682+O682","v":29.2},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,29.2,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,960,"FDCP","FDCP9603HLX     "," ","FDCP4503HLX     ","FDCP5043HLX     ",null,null,"その他",{"$f":"O682+O683","v":30.9},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,30.9,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,1010,"FDCP","FDCP10103HLX     "," ","FDCP5043HLX     ","FDCP5043HLX     ",null,null,"その他",{"$f":"O683+O683","v":32.6},null,"90m未満",15.88,null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,"-主管サイズを超過-",null,0.37,"-主管サイズを超過-",null,"***","-主管サイズを超過-",0,null,0,null,0,0,0,100,32.6,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,1065,"FDCP","FDCP10653HLX     "," ","FDCP5043HLX     ","FDCP5603HLX     ",null,null,"その他",{"$f":"O683+O684","v":33.700000000000003},null,"90m以上",22.22,null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","-主管サイズを超過-",0,null,0,null,0,0,0,100,33.700000000000003,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,1130,"FDCP","FDCP11303HLX     "," ","FDCP5603HLX     ","FDCP5603HLX     ",null,null,"その他",{"$f":"O684+O684","v":34.799999999999997},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,34.799999999999997,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,1180,"FDCP","FDCP11803HLX     "," ","FDCP5603HLX     ","FDCP6153HLX     ",null,null,"その他",{"$f":"O684+O685","v":36},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,36,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,1235,"FDCP","FDCP12353HLX     "," ","FDCP6153HLX     ","FDCP6153HLX     ",null,null,"その他",{"$f":"O685+O685","v":37.200000000000003},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,37.200000000000003,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,1300,"FDCP","FDCP13003HLX     "," ","FDCP6153HLX     ","FDCP6803HLX     ",null,null,"その他",{"$f":"O685+O686","v":38.5},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,38.5,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,1360,"FDCP","FDCP13603HLX     "," ","FDCP6803HLX     ","FDCP6803HLX     ",null,null,"その他",{"$f":"O686+O686","v":39.799999999999997},100,null,"",100,2.1999999999999999E-2,2.1999999999999997,40,5.8999999999999997E-2,2.36,30,0.12,3.5999999999999996,20,0.18,3.5999999999999996,40,0.26,10.4,100,0.37,37,null,"***","0",59.16,null,0,26,0,0,0,100,39.799999999999997,0.39799999999999996,0.39,0.42,0.42,"OK",""]
[null,"R410A",3,null,null,335,"FDCSP","FDCSP3353HLX-K  "," ",null,null,null,null,"その他",11.9,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,11.9,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,400,"FDCSP","FDCSP4003HLX    "," ",null,null,null,null,"その他",12.8,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,12.8,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,450,"FDCSP","FDCSP4503HLX    "," ",null,null,null,null,"その他",14.6,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,14.6,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,504,"FDCSP","FDCSP5043HLX    "," ",null,null,null,null,"その他",16.3,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,16.3,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,560,"FDCSP","FDCSP5603HLX    "," ",null,null,null,null,"その他",17.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,17.399999999999999,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,615,"FDCSP","FDCSP6153HLX    "," ",null,null,null,null,"その他",18.600000000000001,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,18.600000000000001,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,680,"FDCSP","FDCSP6803HLX    "," ",null,null,null,null,"その他",19.899999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,19.899999999999999,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,735,"FDCSP","FDCSP7353HLX     "," ","FDCSP3353HLX-K   ","FDCSP4003HLX     ",null,null,"その他",{"$f":"O699+O700","v":24.700000000000003},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,24.700000000000003,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,800,"FDCSP","FDCSP8003HLX     "," ","FDCSP4003HLX     ","FDCSP4003HLX     ",null,null,"その他",{"$f":"O700+O700","v":25.6},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,25.6,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,850,"FDCSP","FDCSP8503HLX     "," ","FDCSP4003HLX     ","FDCSP4503HLX     ",null,null,"その他",{"$f":"O700+O701","v":27.4},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,27.4,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,900,"FDCSP","FDCSP9003HLX     "," ","FDCSP4503HLX     ","FDCSP4503HLX     ",null,null,"その他",{"$f":"O701+O701","v":29.2},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,29.2,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,960,"FDCSP","FDCSP9603HLX     "," ","FDCSP4503HLX     ","FDCSP5043HLX     ",null,null,"その他",{"$f":"O701+O702","v":30.9},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,30.9,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,1010,"FDCSP","FDCSP10103HLX     "," ","FDCSP5043HLX     ","FDCSP5043HLX     ",null,null,"その他",{"$f":"O702+O702","v":32.6},null,null,{"$f":"IF(Q711=\"\",\"\",IF(Q711=\"90m未満\",VLOOKUP(C711&D711&\",\"&F711,主管サイズルックアップ用,5,FALSE),VLOOKUP(C711&D711&\",\"&F711,主管サイズルックアップ用,6,FALSE)))","v":""},null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,{"$f":"IF(AP711+AS711<0,0,AP711+AS711)","v":0},{"$f":"VLOOKUP(C711&D711&\",\"&F711,封入上限ルックアップ用,5,FALSE)","v":100},{"$f":"O711+AT711","v":32.6},{"$f":"IF(ISERROR(AV711/P711),\"\",AV711/P711)","v":""},0.39,0.42,0.42,{"$f":"IF(AW711=\"\",\"\",IF(OR(AW711<=AX711,AND(N711=\"その他\",AW711<=AY711)),\"OK\",IF(OR(AND(N711=\"最下層\",AW711<=AY711),AND(N711=\"その他\",AW711<=AZ711)),\"対策が１つ必要です\",IF(OR(AND(N711=\"最下層\",AW711<=AZ711),AND(N711=\"その他\",AW711>AZ711)),\"対策が２つ必要です\",\"システムの見直しが必要です\"))))","v":""},""]
[null,"R410A",3,null,null,1065,"FDCSP","FDCSP10653HLX     "," ","FDCSP5043HLX     ","FDCSP5603HLX     ",null,null,"その他",{"$f":"O702+O703","v":33.700000000000003},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,{"$f":"AN712*AO712","v":0},null,0,0,0,100,33.700000000000003,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,1130,"FDCSP","FDCSP11303HLX     "," ","FDCSP5603HLX     ","FDCSP5603HLX     ",null,null,"その他",{"$f":"O703+O703","v":34.799999999999997},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,34.799999999999997,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,1180,"FDCSP","FDCSP11803HLX     "," ","FDCSP5603HLX     ","FDCSP6153HLX     ",null,null,"その他",{"$f":"O703+O704","v":36},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,36,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,1235,"FDCSP","FDCSP12353HLX     "," ","FDCSP6153HLX     ","FDCSP6153HLX     ",null,null,"その他",{"$f":"O704+O704","v":37.200000000000003},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,37.200000000000003,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,1300,"FDCSP","FDCSP13003HLX     "," ","FDCSP6153HLX     ","FDCSP6803HLX     ",null,null,"その他",{"$f":"O704+O705","v":38.5},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,38.5,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,1360,"FDCSP","FDCSP13603HLX     "," ","FDCSP6803HLX     ","FDCSP6803HLX     ",null,null,"その他",{"$f":"O705+O705","v":39.799999999999997},100,null,"",100,2.1999999999999999E-2,2.1999999999999997,40,5.8999999999999997E-2,2.36,30,0.12,3.5999999999999996,20,0.18,3.5999999999999996,40,0.26,10.4,100,0.37,37,null,"***","0",59.16,null,0,26,0,0,0,100,39.799999999999997,0.39799999999999996,0.39,0.42,0.42,"OK",""]
[null,"R410A",3,null,"冷暖フリー",735,"FDCSP","FDCSP7353HLXR    "," ","FDCSP3353HLXR-K  ","FDCSP4003HLXR    ",null,null,"その他",{"$f":"O843+O844","v":0},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,100,0,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,"冷暖フリー",800,"FDCSP","FDCSP8003HLXR    "," ","FDCSP4003HLXR    ","FDCSP4003HLXR    ",null,null,"その他",{"$f":"O844+O844","v":0},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,100,0,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,"冷暖フリー",850,"FDCSP","FDCSP8503HLXR    "," ","FDCSP4003HLXR    ","FDCSP4503HLXR    ",null,null,"その他",{"$f":"O844+O845","v":0},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,100,0,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,"冷暖フリー",900,"FDCSP","FDCSP9003HLXR    "," ","FDCSP4503HLXR    ","FDCSP4503HLXR    ",null,null,"その他",{"$f":"O845+O845","v":0},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,100,0,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,"冷暖フリー",960,"FDCSP","FDCSP9603HLXR    "," ","FDCSP4503HLXR    ","FDCSP5043HLXR    ",null,null,"その他",{"$f":"O845+O846","v":0},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,100,0,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,"冷暖フリー",1010,"FDCSP","FDCSP10103HLXR    "," ","FDCSP5043HLXR    ","FDCSP5043HLXR    ",null,null,"その他",{"$f":"O846+O846","v":0},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,100,0,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,"冷暖フリー",1065,"FDCSP","FDCSP10653HLXR    "," ","FDCSP5043HLXR    ","FDCSP5603HLXR    ",null,null,"その他",{"$f":"O846+O847","v":0},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,100,0,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,"冷暖フリー",1130,"FDCSP","FDCSP11303HLXR    "," ","FDCSP5603HLXR    ","FDCSP5603HLXR    ",null,null,"その他",{"$f":"O847+O847","v":0},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,100,0,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,"冷暖フリー",1180,"FDCSP","FDCSP11803HLXR    "," ","FDCSP5603HLXR    ","FDCSP6153HLXR    ",null,null,"その他",{"$f":"O847+O848","v":0},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,100,0,"",0.39,0.42,{"$f":"IF(B726=\"R410A\",0.42,IF(B726=\"R407C\",0.49,IF(B726=\"R22\",0.5,\"NG\")))","v":0.42},"",""]
[null,"R410A",3,null,"冷暖フリー",1235,"FDCSP","FDCSP12353HLXR    "," ","FDCSP6153HLXR    ","FDCSP6153HLXR    ",null,null,"その他",{"$f":"O848+O848","v":0},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,100,0,"",0.39,0.42,{"$f":"IF(B727=\"R410A\",0.42,IF(B727=\"R407C\",0.49,IF(B727=\"R22\",0.5,\"NG\")))","v":0.42},"",""]
[null,"R410A",3,null,"冷暖フリー",1300,"FDCSP","FDCSP13003HLXR    "," ","FDCSP6153HLXR    ","FDCSP6803HLXR    ",null,null,"その他",{"$f":"O848+O849","v":0},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,100,0,"",0.39,0.42,{"$f":"IF(B728=\"R410A\",0.42,IF(B728=\"R407C\",0.49,IF(B728=\"R22\",0.5,\"NG\")))","v":0.42},"",""]
[null,"R410A",3,null,"冷暖フリー",1360,"FDCSP","FDCSP13603HLXR    "," ","FDCSP6803HLXR    ","FDCSP6803HLXR    ",null,null,"その他",{"$f":"O849+O849","v":0},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,100,0,"",0.39,0.42,{"$f":"IF(B729=\"R410A\",0.42,IF(B729=\"R407C\",0.49,IF(B729=\"R22\",0.5,\"NG\")))","v":0.42},"",""]
[null,"R410A",3,null,null,224,"FDCRP","FDCRP2243HLXY   "," ",null,null,null,null,"その他",14,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,50,14,"",0.39,0.42,{"$f":"IF(B730=\"R410A\",0.42,IF(B730=\"R407C\",0.49,IF(B730=\"R22\",0.5,\"NG\")))","v":0.42},"",""]
[null,"R410A",3,null,null,280,"FDCRP","FDCRP2803HLXY   "," ",null,null,null,null,"その他",14,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,{"$f":"AR731","v":0},0,50,14,"",{"$f":"IF(B731=\"R410A\",0.39,IF(B731=\"R407C\",0.27,IF(B731=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(B731=\"R410A\",0.42,IF(B731=\"R407C\",0.46,IF(B731=\"R22\",0.28,\"NG\")))","v":0.42},{"$f":"IF(B731=\"R410A\",0.42,IF(B731=\"R407C\",0.49,IF(B731=\"R22\",0.5,\"NG\")))","v":0.42},"",""]
[null,"R410A",3,null,null,280,"FDCRP","FDCRP2803HLX-K  "," ",null,null,null,null,"その他",10.4,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,10.4,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,335,"FDCRP","FDCRP3353HLX    "," ",null,null,null,null,"その他",11.9,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,11.9,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,400,"FDCRP","FDCRP4003HLX    "," ",null,null,null,null,"その他",12.8,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,12.8,"",0.39,0.42,0.42,"",{"$f":"IF(AND(C734=3,AT734>AU734),\"追加封入量の上限を超えています\",\"\")","v":""}]
[null,"R410A",3,null,null,450,"FDCRP","FDCRP4503HLX    "," ",null,null,null,null,"その他",14.6,null,null,"",null,2.1999999999999999E-2,{"$f":"IF($R735=\"***\",\"実長90m超使用不可\",IF($R735<6.35,\"-主管サイズを超過-\",IF(T735=\"***\",\"0\",S735*T735)))","v":0},null,5.8999999999999997E-2,{"$f":"IF($R735=\"***\",\"実長90m超使用不可\",IF($R735<9.52,\"-主管サイズを超過-\",IF(W735=\"***\",\"0\",V735*W735)))","v":0},null,0.12,{"$f":"IF($R735=\"***\",\"実長90m超使用不可\",IF($R735<12.7,\"-主管サイズを超過-\",IF(Z735=\"***\",\"0\",Y735*Z735)))","v":0},null,0.18,{"$f":"IF($R735=\"***\",\"実長90m超使用不可\",IF($R735<15.88,\"-主管サイズを超過-\",IF(AC735=\"***\",\"0\",AB735*AC735)))","v":0},null,0.26,{"$f":"IF($R735=\"***\",\"実長90m超使用不可\",IF($R735<19.05,\"-主管サイズを超過-\",IF(AF735=\"***\",\"0\",AE735*AF735)))","v":0},null,0.37,{"$f":"IF($R735=\"***\",\"実長90m超使用不可\",IF($R735<22.22,\"-主管サイズを超過-\",IF(AI735=\"***\",\"0\",AH735*AI735)))","v":0},null,"***",{"$f":"IF($R735=\"***\",\"実長90m超使用不可\",IF($R735<25.4,\"-主管サイズを超過-\",IF(AL735=\"***\",\"0\",AK735*AL735)))","v":"0"},{"$f":"IF(OR(U735=\"実長90m超使用不可\",U735=\"-主管サイズを超過-\"),0,U735)+IF(OR(X735=\"実長90m超使用不可\",X735=\"-主管サイズを超過-\"),0,X735)+IF(OR(AA735=\"実長90m超使用不可\",AA735=\"-主管サイズを超過-\"),0,AA735)+IF(OR(AD735=\"実長90m超使用不可\",AD735=\"-主管サイズを超過-\"),0,AD735)+IF(OR(AG735=\"実長90m超使用不可\",AG735=\"-主管サイズを超過-\"),0,AG735)+IF(OR(AJ735=\"実長90m超使用不可\",AJ735=\"-主管サイズを超過-\"),0,AJ735)+IF(OR(AM735=\"実長90m超使用不可\",AM735=\"-主管サイズを超過-\"),0,AM735)","v":0},null,0,null,0,0,0,50,14.6,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,504,"FDCRP","FDCRP5043HLX    "," ",null,null,null,null,"その他",17.8,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,17.8,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,560,"FDCRP","FDCRP5603HLX    "," ",null,null,null,null,"その他",18.899999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,18.899999999999999,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,615,"FDCRP","FDCRP6153HLX    "," ","FDCRP2803HLX-K  ","FDCRP3353HLX    ",null,null,"その他",{"$f":"O732+O733","v":22.3},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",{"$f":"IF(OR(U738=\"実長90m超使用不可\",U738=\"-主管サイズを超過-\"),0,U738)+IF(OR(X738=\"実長90m超使用不可\",X738=\"-主管サイズを超過-\"),0,X738)+IF(OR(AA738=\"実長90m超使用不可\",AA738=\"-主管サイズを超過-\"),0,AA738)+IF(OR(AD738=\"実長90m超使用不可\",AD738=\"-主管サイズを超過-\"),0,AD738)+IF(OR(AG738=\"実長90m超使用不可\",AG738=\"-主管サイズを超過-\"),0,AG738)+IF(OR(AJ738=\"実長90m超使用不可\",AJ738=\"-主管サイズを超過-\"),0,AJ738)+IF(OR(AM738=\"実長90m超使用不可\",AM738=\"-主管サイズを超過-\"),0,AM738)","v":0},null,0,null,0,0,0,50,22.3,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,680,"FDCRP","FDCRP6803HLX    "," ","FDCRP3353HLX    ","FDCRP3353HLX    ",null,null,"その他",{"$f":"O733+O733","v":23.8},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,23.8,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,735,"FDCRP","FDCRP7353HLX    "," ","FDCRP3353HLX    ","FDCRP4003HLX    ",null,null,"その他",{"$f":"O733+O734","v":24.700000000000003},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,24.700000000000003,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,800,"FDCRP","FDCRP8003HLX    "," ","FDCRP4003HLX    ","FDCRP4003HLX    ",null,null,"その他",{"$f":"O734+O734","v":25.6},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,25.6,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,850,"FDCRP","FDCRP8503HLX    "," ","FDCRP4003HLX    ","FDCRP4503HLX    ",null,null,"その他",{"$f":"O734+O735","v":27.4},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,27.4,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,900,"FDCRP","FDCRP9003HLX    "," ","FDCRP4503HLX    ","FDCRP4503HLX    ",null,null,"その他",{"$f":"O735+O735","v":29.2},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,{"$f":"VLOOKUP(C743&D743&\",\"&F743,封入上限ルックアップ用,5,FALSE)","v":100},29.2,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,960,"FDCRP","FDCRP9603HLX    "," ","FDCRP4503HLX    ","FDCRP5043HLX    ",null,null,"その他",{"$f":"O735+O736","v":32.4},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,32.4,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,1010,"FDCRP","FDCRP10103HLX    "," ","FDCRP5043HLX    ","FDCRP5043HLX    ",null,null,"その他",{"$f":"O736+O736","v":35.6},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,35.6,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,224,"FDCRSP","FDCRSP2243HLXY  "," ",null,null,null,null,"その他",14,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,50,14,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,280,"FDCRSP","FDCRSP2803HLXY  "," ",null,null,null,null,"その他",14,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,{"$f":"AR747","v":0},0,50,14,"",{"$f":"IF(B747=\"R410A\",0.39,IF(B747=\"R407C\",0.27,IF(B747=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(B747=\"R410A\",0.42,IF(B747=\"R407C\",0.46,IF(B747=\"R22\",0.28,\"NG\")))","v":0.42},{"$f":"IF(B747=\"R410A\",0.42,IF(B747=\"R407C\",0.49,IF(B747=\"R22\",0.5,\"NG\")))","v":0.42},"",""]
[null,"R410A",3,null,null,280,"FDCRSP","FDCRSP2803HLX-K "," ",null,null,null,null,"その他",10.4,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,10.4,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,335,"FDCRSP","FDCRSP3353HLX   "," ",null,null,null,null,"その他",11.9,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,11.9,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,400,"FDCRSP","FDCRSP4003HLX   "," ",null,null,null,null,"その他",12.8,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,12.8,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,450,"FDCRSP","FDCRSP4503HLX   "," ",null,null,null,null,"その他",14.6,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,14.6,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,504,"FDCRSP","FDCRSP5043HLX   "," ",null,null,null,null,"その他",17.8,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,17.8,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,560,"FDCRSP","FDCRSP5603HLX   "," ",null,null,null,null,"その他",18.899999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,18.899999999999999,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,615,"FDCRSP","FDCRSP6153HLX    "," ","FDCRSP2803HLX-K  ","FDCRSP3353HLX    ",null,null,"その他",{"$f":"O748+O749","v":22.3},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,22.3,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,680,"FDCRSP","FDCRSP6803HLX    "," ","FDCRSP3353HLX    ","FDCRSP3353HLX    ",null,null,"その他",{"$f":"O749+O749","v":23.8},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,23.8,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,735,"FDCRSP","FDCRSP7353HLX    "," ","FDCRSP3353HLX    ","FDCRSP4003HLX    ",null,null,"その他",{"$f":"O749+O750","v":24.700000000000003},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,24.700000000000003,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,800,"FDCRSP","FDCRSP8003HLX    "," ","FDCRSP4003HLX    ","FDCRSP4003HLX    ",null,null,"その他",{"$f":"O750+O750","v":25.6},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,25.6,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,850,"FDCRSP","FDCRSP8503HLX    "," ","FDCRSP4003HLX    ","FDCRSP4503HLX    ",null,null,"その他",{"$f":"O750+O751","v":27.4},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,{"$f":"AR758","v":0},0,100,27.4,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,900,"FDCRSP","FDCRSP9003HLX    "," ","FDCRSP4503HLX    ","FDCRSP4503HLX    ",null,null,"その他",{"$f":"O751+O751","v":29.2},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,29.2,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,960,"FDCRSP","FDCRSP9603HLX    "," ","FDCRSP4503HLX    ","FDCRSP5043HLX    ",null,null,"その他",{"$f":"O751+O752","v":32.4},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,32.4,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,1010,"FDCRSP","FDCRSP10103HLX    "," ","FDCRSP5043HLX    ","FDCRSP5043HLX    ",null,null,"その他",{"$f":"O752+O752","v":35.6},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,100,35.6,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,160,"FDCP","FDCP1603HLXYA   "," ",null,null,null,null,"その他",11.5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,2.5,2.5,2.5,50,14,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,224,"FDCP","FDCP2243HLXYA   "," ",null,null,null,null,"その他",11.5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,2.5,2.5,2.5,50,14,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,280,"FDCP","FDCP2803HLXYA   "," ",null,null,null,null,"その他",11.5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,2.5,2.5,2.5,50,14,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,335,"FDCP","FDCP3353HLXYA   "," ",null,null,null,null,"その他",11.5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,2.5,2.5,2.5,50,14,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,224,"FDCRP","FDCRP2243HLXYA  "," ",null,null,null,null,"その他",11.5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,2.5,2.5,2.5,50,14,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,280,"FDCRP","FDCRP2803HLXYA  "," ",null,null,null,null,"その他",11.5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,2.5,2.5,2.5,50,14,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,224,"FDCRSP","FDCRSP2243HLXYA "," ",null,null,null,null,"その他",11.5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,2.5,2.5,2.5,50,14,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,280,"FDCRSP","FDCRSP2803HLXYA "," ",null,null,null,null,"その他",11.5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,2.5,2.5,2.5,50,14,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,160,"FDCSP","FDCSP1603HLXYA  "," ",null,null,null,null,"その他",11.5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,2.5,2.5,2.5,50,14,"",{"$f":"IF(B770=\"R410A\",0.39,IF(B770=\"R407C\",0.27,IF(B770=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(B770=\"R410A\",0.42,IF(B770=\"R407C\",0.46,IF(B770=\"R22\",0.28,\"NG\")))","v":0.42},0.42,"",""]
[null,"R410A",3,null,null,224,"FDCSP","FDCSP2243HLXYA  "," ",null,null,null,null,"その他",11.5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,2.5,2.5,2.5,50,14,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,280,"FDCSP","FDCSP2803HLXYA  "," ",null,null,null,null,"その他",11.5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,2.5,2.5,2.5,50,14,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,335,"FDCSP","FDCSP3353HLXYA  "," ",null,null,null,null,"その他",11.5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,null,0,null,2.5,2.5,2.5,50,14,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,112,"FDCP","FDCP1123HLX     ","A",null,null,null,null,"その他",5,null,"90m以上","***",null,2.1999999999999999E-2,"実長90m超使用不可",null,5.3999999999999999E-2,"実長90m超使用不可",null,"***","実長90m超使用不可",null,"***","実長90m超使用不可",null,"***","実長90m超使用不可",null,"***","実長90m超使用不可",null,"***","実長90m超使用不可",0,null,0,null,{"$f":"3.38-O774","v":-1.62},-1.62,0,50,5,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,140,"FDCP","FDCP1403HLX     ","A",null,null,null,null,"その他",5,null,null,{"$f":"IF(Q775=\"\",\"\",IF(Q775=\"90m未満\",VLOOKUP(C775&D775&\",\"&F775,主管サイズルックアップ用,5,FALSE),VLOOKUP(C775&D775&\",\"&F775,主管サイズルックアップ用,6,FALSE)))","v":""},null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,{"$f":"3.38-O775","v":-1.62},-1.62,{"$f":"IF(AP775+AS775<0,0,AP775+AS775)","v":0},50,{"$f":"O775+AT775","v":5},{"$f":"IF(ISERROR(AV775/P775),\"\",AV775/P775)","v":""},0.39,0.42,0.42,{"$f":"IF(AW775=\"\",\"\",IF(OR(AW775<=AX775,AND(N775=\"その他\",AW775<=AY775)),\"OK\",IF(OR(AND(N775=\"最下層\",AW775<=AY775),AND(N775=\"その他\",AW775<=AZ775)),\"対策が１つ必要です\",IF(OR(AND(N775=\"最下層\",AW775<=AZ775),AND(N775=\"その他\",AW775>AZ775)),\"対策が２つ必要です\",\"システムの見直しが必要です\"))))","v":""},""]
[null,"R410A",3,null,null,112,"FDCSP","FDCSP1123HLX    ","A",null,null,null,null,"その他",5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,{"$f":"AN776*AO776","v":0},null,{"$f":"3.38-O776","v":-1.62},-1.62,0,50,5,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,140,"FDCSP","FDCSP1403HLX    ","A",null,null,null,null,"その他",5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,{"$f":"3.38-O777","v":-1.62},-1.62,0,50,5,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,280,"FDCRP","FDCRP2803HLX-K  ","T",null,null,null,null,"その他",10.4,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,10.4,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,160,"FDCP","FDCP1603HLX     "," ",null,null,null,null,"その他",5.34,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,50,5.34,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,160,"FDCSP","FDCSP1603HLX    "," ",null,null,null,null,"その他",5.34,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,null,0,null,0,0,0,50,5.34,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,280,"FDCRP","FDCRP2803HLXA-K "," ",null,null,null,null,"その他",10.4,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,10.4,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,335,"FDCRP","FDCRP3353HLXA   "," ",null,null,null,null,"その他",11.9,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,11.9,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,400,"FDCRP","FDCRP4003HLXA   "," ",null,null,null,null,"その他",12.8,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,12.8,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,450,"FDCRP","FDCRP4503HLXA   "," ",null,null,null,null,"その他",14.6,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,14.6,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,504,"FDCRP","FDCRP5043HLXA   "," ",null,null,null,null,"その他",17.8,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,17.8,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,560,"FDCRP","FDCRP5603HLXA   "," ",null,null,null,null,"その他",18.899999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,18.899999999999999,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,280,"FDCRSP","FDCRSP2803HLXA-K"," ",null,null,null,null,"その他",10.4,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,10.4,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,335,"FDCRSP","FDCRSP3353HLXA  "," ",null,null,null,null,"その他",11.9,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,11.9,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,400,"FDCRSP","FDCRSP4003HLXA  "," ",null,null,null,null,"その他",12.8,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,12.8,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,450,"FDCRSP","FDCRSP4503HLXA  "," ",null,null,null,null,"その他",14.6,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,14.6,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,504,"FDCRSP","FDCRSP5043HLXA  "," ",null,null,null,null,"その他",17.8,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,17.8,"",0.39,0.42,0.42,"",""]
[null,"R410A",3,null,null,560,"FDCRSP","FDCRSP5603HLXA  "," ",null,null,null,null,"その他",18.899999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,null,0,null,0,0,0,50,18.899999999999999,"",0.39,0.42,0.42,"",""]
["10年7月","R410A",3,null,null,112,"FDCP","FDCP1123HLXB    "," ",null,null,null,null,"その他",5,200,"90m未満",9.52,10,2.1999999999999999E-2,0.21999999999999997,10,5.3999999999999999E-2,0.54,null,"***","-主管サイズを超過-",null,"***","-主管サイズを超過-",null,"***","-主管サイズを超過-",null,"***","-主管サイズを超過-",null,"***","-主管サイズを超過-",0.76,1,0.76,2,{"$f":"3.38-O793","v":-1.62},-1.62,0,50,5,2.5000000000000001E-2,0.39,0.42,0.42,"OK",""]
["10年7月","R410A",3,null,null,140,"FDCP","FDCP1403HLXB    "," ",null,null,null,null,"その他",5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,1,0,null,{"$f":"3.38-O794","v":-1.62},-1.62,0,50,5,"",0.39,0.42,{"$f":"IF(B794=\"R410A\",0.42,IF(B794=\"R407C\",0.49,IF(B794=\"R22\",0.5,\"NG\")))","v":0.42},"",""]
["10年7月","R410A",3,null,null,160,"FDCP","FDCP1603HLXB    "," ",null,null,null,null,"その他",5.34,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,1,0,null,0,0,0,50,5.34,"",0.39,0.42,0.42,"",""]
["10年7月","R410A",3,null,null,224,"FDCP","FDCP2243HLXYB   "," ",null,null,null,null,"その他",11.5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,1,{"$f":"AN796*AO796","v":0},null,2.5,{"$f":"AR796","v":2.5},2.5,{"$f":"VLOOKUP(C796&D796&\",\"&F796,封入上限ルックアップ用,5,FALSE)","v":50},14,"",{"$f":"IF(B796=\"R410A\",0.39,IF(B796=\"R407C\",0.27,IF(B796=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(B796=\"R410A\",0.42,IF(B796=\"R407C\",0.46,IF(B796=\"R22\",0.28,\"NG\")))","v":0.42},0.42,"",""]
["10年7月","R410A",3,null,null,280,"FDCP","FDCP2803HLXYB   "," ",null,null,null,null,"その他",11.5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,1,{"$f":"AN797*AO797","v":0},null,2.5,{"$f":"AR797","v":2.5},2.5,{"$f":"VLOOKUP(C797&D797&\",\"&F797,封入上限ルックアップ用,5,FALSE)","v":50},14,"",{"$f":"IF(B797=\"R410A\",0.39,IF(B797=\"R407C\",0.27,IF(B797=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(B797=\"R410A\",0.42,IF(B797=\"R407C\",0.46,IF(B797=\"R22\",0.28,\"NG\")))","v":0.42},0.42,"",""]
["10年7月","R410A",3,null,null,335,"FDCP","FDCP3353HLXYB   "," ",null,null,null,null,"その他",11.5,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,1,{"$f":"AN798*AO798","v":0},null,2.5,{"$f":"AR798","v":2.5},2.5,{"$f":"VLOOKUP(C798&D798&\",\"&F798,封入上限ルックアップ用,5,FALSE)","v":50},14,"",{"$f":"IF(B798=\"R410A\",0.39,IF(B798=\"R407C\",0.27,IF(B798=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(B798=\"R410A\",0.42,IF(B798=\"R407C\",0.46,IF(B798=\"R22\",0.28,\"NG\")))","v":0.42},0.42,"",{"$f":"IF(AND(C798=3,AT798>AU798),\"追加封入量の上限を超えています\",\"\")","v":""}]
["10年7月","R410A",3,null,null,335,"FDCP","FDCP3353HLXB-K  "," ",null,null,null,null,"その他",11.9,null,null,"",null,2.1999999999999999E-2,{"$f":"IF($R799=\"***\",\"実長90m超使用不可\",IF($R799<6.35,\"-主管サイズを超過-\",IF(T799=\"***\",\"0\",S799*T799)))","v":0},null,5.8999999999999997E-2,{"$f":"IF($R799=\"***\",\"実長90m超使用不可\",IF($R799<9.52,\"-主管サイズを超過-\",IF(W799=\"***\",\"0\",V799*W799)))","v":0},null,0.12,{"$f":"IF($R799=\"***\",\"実長90m超使用不可\",IF($R799<12.7,\"-主管サイズを超過-\",IF(Z799=\"***\",\"0\",Y799*Z799)))","v":0},null,0.18,{"$f":"IF($R799=\"***\",\"実長90m超使用不可\",IF($R799<15.88,\"-主管サイズを超過-\",IF(AC799=\"***\",\"0\",AB799*AC799)))","v":0},null,0.26,{"$f":"IF($R799=\"***\",\"実長90m超使用不可\",IF($R799<19.05,\"-主管サイズを超過-\",IF(AF799=\"***\",\"0\",AE799*AF799)))","v":0},null,0.37,{"$f":"IF($R799=\"***\",\"実長90m超使用不可\",IF($R799<22.22,\"-主管サイズを超過-\",IF(AI799=\"***\",\"0\",AH799*AI799)))","v":0},null,"***",{"$f":"IF($R799=\"***\",\"実長90m超使用不可\",IF($R799<25.4,\"-主管サイズを超過-\",IF(AL799=\"***\",\"0\",AK799*AL799)))","v":"0"},{"$f":"IF(OR(U799=\"実長90m超使用不可\",U799=\"-主管サイズを超過-\"),0,U799)+IF(OR(X799=\"実長90m超使用不可\",X799=\"-主管サイズを超過-\"),0,X799)+IF(OR(AA799=\"実長90m超使用不可\",AA799=\"-主管サイズを超過-\"),0,AA799)+IF(OR(AD799=\"実長90m超使用不可\",AD799=\"-主管サイズを超過-\"),0,AD799)+IF(OR(AG799=\"実長90m超使用不可\",AG799=\"-主管サイズを超過-\"),0,AG799)+IF(OR(AJ799=\"実長90m超使用不可\",AJ799=\"-主管サイズを超過-\"),0,AJ799)+IF(OR(AM799=\"実長90m超使用不可\",AM799=\"-主管サイズを超過-\"),0,AM799)","v":0},1,0,null,0,0,0,50,11.9,"",0.39,0.42,0.42,"",""]
["10年7月","R410A",3,null,null,400,"FDCP","FDCP4003HLXB    "," ",null,null,null,null,"その他",12.8,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,50,12.8,"",0.39,0.42,0.42,"",""]
["10年7月","R410A",3,null,null,450,"FDCP","FDCP4503HLXB    "," ",null,null,null,null,"その他",14.6,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,50,14.6,"",0.39,0.42,0.42,"",""]
["10年7月","R410A",3,null,null,504,"FDCP","FDCP5043HLXB    "," ",null,null,null,null,"その他",16.3,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,50,16.3,"",0.39,0.42,0.42,"",""]
["10年7月","R410A",3,null,null,560,"FDCP","FDCP5603HLXB    "," ",null,null,null,null,"その他",17.399999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,50,17.399999999999999,"",0.39,0.42,0.42,"",""]
["10年7月","R410A",3,null,null,615,"FDCP","FDCP6153HLXB    "," ",null,null,null,null,"その他",18.600000000000001,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,50,18.600000000000001,"",0.39,0.42,0.42,"",""]
["10年7月","R410A",3,null,null,680,"FDCP","FDCP6803HLXB    "," ",null,null,null,null,"その他",19.899999999999999,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,50,19.899999999999999,"",0.39,0.42,0.42,"",""]
["10年7月","R410A",3,null,null,735,"FDCP","FDCP7353HLXB",null,"FDCP3353HLXB-K  ","FDCP4003HLXB    ",null,null,null,{"$f":"O799+O800","v":24.700000000000003},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,100,24.700000000000003,"",0.39,0.42,0.42,"",""]
["10年7月","R410A",3,null,null,800,"FDCP","FDCP8003HLXB",null,"FDCP4003HLXB    ","FDCP4003HLXB    ",null,null,null,{"$f":"O800+O800","v":25.6},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,100,25.6,"",0.39,0.42,0.42,"",""]
["10年7月","R410A",3,null,null,850,"FDCP","FDCP8503HLXB",null,"FDCP4003HLXB    ","FDCP4503HLXB    ",null,null,null,{"$f":"O800+O801","v":27.4},null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,100,27.4,"",0.39,0.42,0.42,"",""]
["10年7月",null,3,null,null,null,null,null,null,"FDCP4503HLXB    ","FDCP4503HLXB    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null,null,"FDCP4503HLXB    ","FDCP5043HLXB    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null,null,"FDCP5043HLXB    ","FDCP5043HLXB    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null,null,"FDCP5043HLXB    ","FDCP5603HLXB    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null,null,"FDCP5603HLXB    ","FDCP5603HLXB    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null,null,"FDCP5603HLXB    ","FDCP6153HLXB    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null,null,"FDCP6153HLXB    ","FDCP6153HLXB    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null,null,"FDCP6153HLXB    ","FDCP6803HLXB    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null,null,"FDCP6803HLXB    ","FDCP6803HLXB    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$f":"VLOOKUP(C818&D818&\",\"&F818,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,{"$f":"AR822","v":0},0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ","FDCP3353HLXR-K  ","FDCP4003HLXR    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ","FDCP4003HLXR    ","FDCP4003HLXR    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ","FDCP4003HLXR    ","FDCP4503HLXR    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ","FDCP4503HLXR    ","FDCP4503HLXR    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ","FDCP4503HLXR    ","FDCP5043HLXR    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ","FDCP5043HLXR    ","FDCP5043HLXR    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ","FDCP5043HLXR    ","FDCP5603HLXR    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ","FDCP5603HLXR    ","FDCP5603HLXR    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ","FDCP5603HLXR    ","FDCP6153HLXR    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ","FDCP6153HLXR    ","FDCP6153HLXR    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ","FDCP6153HLXR    ","FDCP6803HLXR    ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ","FDCP6803HLXR    ","FDCP6803HLXR    ",null,null,null,null,null,null,{"$f":"IF(Q839=\"\",\"\",IF(Q839=\"90m未満\",VLOOKUP(C839&D839&\",\"&F839,主管サイズルックアップ用,5,FALSE),VLOOKUP(C839&D839&\",\"&F839,主管サイズルックアップ用,6,FALSE)))","v":""},null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.2,0,null,0,0,{"$f":"IF(AP839+AS839<0,0,AP839+AS839)","v":0},{"$error":"#N/A"},{"$f":"O839+AT839","v":0},{"$f":"IF(ISERROR(AV839/P839),\"\",AV839/P839)","v":""},"NG","NG","NG",{"$f":"IF(AW839=\"\",\"\",IF(OR(AW839<=AX839,AND(N839=\"その他\",AW839<=AY839)),\"OK\",IF(OR(AND(N839=\"最下層\",AW839<=AY839),AND(N839=\"その他\",AW839<=AZ839)),\"対策が１つ必要です\",IF(OR(AND(N839=\"最下層\",AW839<=AZ839),AND(N839=\"その他\",AW839>AZ839)),\"対策が２つ必要です\",\"システムの見直しが必要です\"))))","v":""},{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,"冷暖フリー",null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1.3,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,1,0,null,2.5,{"$f":"AR850","v":2.5},2.5,{"$error":"#N/A"},2.5,"",{"$f":"IF(B850=\"R410A\",0.39,IF(B850=\"R407C\",0.27,IF(B850=\"R22\",0.21,\"NG\")))","v":"NG"},{"$f":"IF(B850=\"R410A\",0.42,IF(B850=\"R407C\",0.46,IF(B850=\"R22\",0.28,\"NG\")))","v":"NG"},"NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,1,0,null,2.5,2.5,2.5,{"$error":"#N/A"},2.5,"",{"$f":"IF(B851=\"R410A\",0.39,IF(B851=\"R407C\",0.27,IF(B851=\"R22\",0.21,\"NG\")))","v":"NG"},{"$f":"IF(B851=\"R410A\",0.42,IF(B851=\"R407C\",0.46,IF(B851=\"R22\",0.28,\"NG\")))","v":"NG"},"NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$f":"VLOOKUP(C856&D856&\",\"&F856,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null,null,"FDCRP2803HLXB-K ","FDCRP3353HLXB   ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$f":"VLOOKUP(C858&D858&\",\"&F858,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},0,"","NG","NG",{"$f":"IF(B858=\"R410A\",0.42,IF(B858=\"R407C\",0.49,IF(B858=\"R22\",0.5,\"NG\")))","v":"NG"},"",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null,null,"FDCRP3353HLXB   ","FDCRP3353HLXB   ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null,null,"FDCRP3353HLXB   ","FDCRP4003HLXB   ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null,null,"FDCRP4003HLXB   ","FDCRP4003HLXB   ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null,null,"FDCRP4003HLXB   ","FDCRP4503HLXB   ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$f":"IF(AND(C862=3,AT862>AU862),\"追加封入量の上限を超えています\",\"\")","v":{"$error":"#N/A"}}]
["10年7月",null,3,null,null,null,null,null,null,"FDCRP4503HLXB   ","FDCRP4503HLXB   ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,{"$f":"IF($R863=\"***\",\"実長90m超使用不可\",IF($R863<6.35,\"-主管サイズを超過-\",IF(T863=\"***\",\"0\",S863*T863)))","v":0},null,5.8999999999999997E-2,{"$f":"IF($R863=\"***\",\"実長90m超使用不可\",IF($R863<9.52,\"-主管サイズを超過-\",IF(W863=\"***\",\"0\",V863*W863)))","v":0},null,0.12,{"$f":"IF($R863=\"***\",\"実長90m超使用不可\",IF($R863<12.7,\"-主管サイズを超過-\",IF(Z863=\"***\",\"0\",Y863*Z863)))","v":0},null,0.18,{"$f":"IF($R863=\"***\",\"実長90m超使用不可\",IF($R863<15.88,\"-主管サイズを超過-\",IF(AC863=\"***\",\"0\",AB863*AC863)))","v":0},null,0.26,{"$f":"IF($R863=\"***\",\"実長90m超使用不可\",IF($R863<19.05,\"-主管サイズを超過-\",IF(AF863=\"***\",\"0\",AE863*AF863)))","v":0},null,0.37,{"$f":"IF($R863=\"***\",\"実長90m超使用不可\",IF($R863<22.22,\"-主管サイズを超過-\",IF(AI863=\"***\",\"0\",AH863*AI863)))","v":0},null,"***",{"$f":"IF($R863=\"***\",\"実長90m超使用不可\",IF($R863<25.4,\"-主管サイズを超過-\",IF(AL863=\"***\",\"0\",AK863*AL863)))","v":"0"},{"$f":"IF(OR(U863=\"実長90m超使用不可\",U863=\"-主管サイズを超過-\"),0,U863)+IF(OR(X863=\"実長90m超使用不可\",X863=\"-主管サイズを超過-\"),0,X863)+IF(OR(AA863=\"実長90m超使用不可\",AA863=\"-主管サイズを超過-\"),0,AA863)+IF(OR(AD863=\"実長90m超使用不可\",AD863=\"-主管サイズを超過-\"),0,AD863)+IF(OR(AG863=\"実長90m超使用不可\",AG863=\"-主管サイズを超過-\"),0,AG863)+IF(OR(AJ863=\"実長90m超使用不可\",AJ863=\"-主管サイズを超過-\"),0,AJ863)+IF(OR(AM863=\"実長90m超使用不可\",AM863=\"-主管サイズを超過-\"),0,AM863)","v":0},1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null,null,"FDCRP4503HLXB   ","FDCRP5043HLXB   ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null,null,"FDCRP5043HLXB   ","FDCRP5043HLXB   ",null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,1,{"$f":"AN866*AO866","v":0},null,2.5,2.5,2.5,{"$f":"VLOOKUP(C866&D866&\",\"&F866,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},2.5,"",{"$f":"IF(B866=\"R410A\",0.39,IF(B866=\"R407C\",0.27,IF(B866=\"R22\",0.21,\"NG\")))","v":"NG"},{"$f":"IF(B866=\"R410A\",0.42,IF(B866=\"R407C\",0.46,IF(B866=\"R22\",0.28,\"NG\")))","v":"NG"},"NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,1,{"$f":"AN867*AO867","v":0},null,2.5,2.5,2.5,{"$f":"VLOOKUP(C867&D867&\",\"&F867,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},2.5,"",{"$f":"IF(B867=\"R410A\",0.39,IF(B867=\"R407C\",0.27,IF(B867=\"R22\",0.21,\"NG\")))","v":"NG"},{"$f":"IF(B867=\"R410A\",0.42,IF(B867=\"R407C\",0.46,IF(B867=\"R22\",0.28,\"NG\")))","v":"NG"},"NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,1,0,null,{"$f":"3.38-O874","v":3.38},3.38,3.38,{"$error":"#N/A"},3.38,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,1,0,null,{"$f":"3.38-O875","v":3.38},3.38,3.38,{"$error":"#N/A"},3.38,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,1,{"$f":"AN877*AO877","v":0},null,2.5,2.5,2.5,{"$f":"VLOOKUP(C877&D877&\",\"&F877,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},2.5,"",{"$f":"IF(B877=\"R410A\",0.39,IF(B877=\"R407C\",0.27,IF(B877=\"R22\",0.21,\"NG\")))","v":"NG"},{"$f":"IF(B877=\"R410A\",0.42,IF(B877=\"R407C\",0.46,IF(B877=\"R22\",0.28,\"NG\")))","v":"NG"},"NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,1,{"$f":"AN878*AO878","v":0},null,2.5,2.5,2.5,{"$f":"VLOOKUP(C878&D878&\",\"&F878,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},2.5,"",{"$f":"IF(B878=\"R410A\",0.39,IF(B878=\"R407C\",0.27,IF(B878=\"R22\",0.21,\"NG\")))","v":"NG"},{"$f":"IF(B878=\"R410A\",0.42,IF(B878=\"R407C\",0.46,IF(B878=\"R22\",0.28,\"NG\")))","v":"NG"},"NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,1,{"$f":"AN879*AO879","v":0},null,2.5,2.5,2.5,{"$f":"VLOOKUP(C879&D879&\",\"&F879,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},2.5,"",{"$f":"IF(B879=\"R410A\",0.39,IF(B879=\"R407C\",0.27,IF(B879=\"R22\",0.21,\"NG\")))","v":"NG"},{"$f":"IF(B879=\"R410A\",0.42,IF(B879=\"R407C\",0.46,IF(B879=\"R22\",0.28,\"NG\")))","v":"NG"},"NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,null,null,null,null,null," ",null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.8999999999999997E-2,0,null,0.12,0,null,0.18,0,null,0.26,0,null,0.37,0,null,"***","0",0,1,0,null,0,0,0,{"$error":"#N/A"},0,"","NG","NG","NG","",{"$error":"#N/A"}]
["10年7月",null,3,"寒冷地",null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,"***","0",null,"***","0",null,"***","0",null,"***","0",null,"***","0",0,1,0,null,0,0,0,{"$f":"VLOOKUP(C887&D887&\",\"&F887,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},0,"",{"$f":"IF(B887=\"R410A\",0.39,IF(B887=\"R407C\",0.27,IF(B887=\"R22\",0.21,\"NG\")))","v":"NG"},{"$f":"IF(B887=\"R410A\",0.42,IF(B887=\"R407C\",0.46,IF(B887=\"R22\",0.28,\"NG\")))","v":"NG"},{"$f":"IF(B887=\"R410A\",0.42,IF(B887=\"R407C\",0.49,IF(B887=\"R22\",0.5,\"NG\")))","v":"NG"},"",{"$error":"#N/A"}]
["10年7月",null,3,"寒冷地",null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,1,0,null,2.5,2.5,2.5,{"$f":"VLOOKUP(C888&D888&\",\"&F888,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},2.5,"",{"$f":"IF(B888=\"R410A\",0.39,IF(B888=\"R407C\",0.27,IF(B888=\"R22\",0.21,\"NG\")))","v":"NG"},{"$f":"IF(B888=\"R410A\",0.42,IF(B888=\"R407C\",0.46,IF(B888=\"R22\",0.28,\"NG\")))","v":"NG"},{"$f":"IF(B888=\"R410A\",0.42,IF(B888=\"R407C\",0.49,IF(B888=\"R22\",0.5,\"NG\")))","v":"NG"},"",{"$error":"#N/A"}]
["10年7月",null,3,"寒冷地",null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,2.1999999999999999E-2,0,null,5.3999999999999999E-2,0,null,0.11,0,null,0.17,0,null,"***","0",null,"***","0",null,"***","0",0,1,{"$f":"AN889*AO889","v":0},null,2.5,2.5,2.5,{"$f":"VLOOKUP(C889&D889&\",\"&F889,封入上限ルックアップ用,5,FALSE)","v":{"$error":"#N/A"}},2.5,"",{"$f":"IF(B889=\"R410A\",0.39,IF(B889=\"R407C\",0.27,IF(B889=\"R22\",0.21,\"NG\")))","v":"NG"},{"$f":"IF(B889=\"R410A\",0.42,IF(B889=\"R407C\",0.46,IF(B889=\"R22\",0.28,\"NG\")))","v":"NG"},{"$f":"IF(B889=\"R410A\",0.42,IF(B889=\"R407C\",0.49,IF(B889=\"R22\",0.5,\"NG\")))","v":"NG"},"",{"$error":"#N/A"}]

{"sheet":"MHI(簡易版)","index":3,"n_rows":865,"n_cols":31,"rows_kept":865,"cut":false,"hidden":true,"merged":[[0,26,0,28],[0,29,2,29],[0,30,2,30]]}
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"C","D","E","限界濃度",null,null,"判定","条件(備考)"]
[null,null,null,null,null,null,null,"B","A",null,null,"φ6.4","φ9.5","φ12.7","φ15.9","φ19.1","φ22.2","φ25.4",null,null,null,null,null,"現地","システム","D/A","RCL","QLMV","ODL"]
["冷媒種","機種名","仕区","組合せ機種",null,null,null,"出荷時\n充てん量","室内容積（ｍ３）","配管径","長さ（ｍ）","係数","係数","係数","係数","係数","係数","係数","重量①","室内機\n台数","室内機設置階　　（地下の　[最下層]　or　[その他]　で選択","係数","重量②","①+②","充てん量\n(B+C)","冷媒濃度"]
["◆１：選択","◆１：選択",null,null,null,null,null,null,"◆２：Input","◆３：選択","◆４：Input",null,null,null,null,null,null,null,null,"◆５：Input","◆６：選択"]
[]
["R22","FDCJ280HKXI2    "," ","ISU13KX2","FDCJ280HKXI2    ",null,null,11,null,null,null,0.03,0.06,0.12,"***","***","***","***",{"$f":"IF(J6=\"φ6.4\",K6*L6,IF(J6=\"φ9.5\",K6*M6,IF(J6=\"φ12.7\",K6*N6,IF(J6=\"φ15.9\",K6*O6,IF(J6=\"φ19.1\",K6*P6,IF(J6=\"φ22.2\",K6*Q6,IF(J6=\"φ25.4\",K6*R6,0)))))))","v":0},null,"その他",17.399999999999999,{"$f":"V6","v":17.399999999999999},{"$f":"IF(S6+W6<0,0,S6+W6)","v":17.399999999999999},{"$f":"H6+X6","v":28.4},{"$f":"Y6/I6","v":{"$error":"#DIV/0!"}},{"$f":"IF(A6=\"R410A\",0.39,IF(A6=\"R407C\",0.27,IF(A6=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A6=\"R410A\",0.42,IF(A6=\"R407C\",0.46,IF(A6=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(A6=\"R410A\",0.42,IF(A6=\"R407C\",0.49,IF(A6=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(OR(Z6<=AA6,AND(U6=\"その他\",Z6<=AB6)),\"OK\",IF(OR(AND(U6=\"最下層\",Z6<=AB6),AND(U6=\"その他\",Z6<=AC6)),\"対策が１つ必要です\",IF(OR(AND(U6=\"最下層\",Z6<=AC6),AND(U6=\"その他\",Z6>AC6)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R22","FDCJ355HKXI2    "," ","ISU16KX2","FDCJ355HKXI2    ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",{"$f":"IF(T7<=8,12,IF(T7<=13,12+(ROUNDDOWN(T7,0)-8)*0.5,\"台数ｵｰﾊﾞ\"))","v":12},12,12,32,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ280HKXI2   "," ","ISU13KX2","FDCSJ280HKXI2   ",null,null,11,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",17.399999999999999,17.399999999999999,17.399999999999999,28.4,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ355HKXI2   "," ","ISU16KX2","FDCSJ355HKXI2   ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",{"$f":"IF(T9<=8,12,IF(T9<=13,12+(ROUNDDOWN(T9,0)-8)*0.5,\"台数ｵｰﾊﾞ\"))","v":12},12,12,32,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ140HKX2A    "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ160HKX2A    "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ224HKX2A    "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ280HKX2A    "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ355HKXA     "," ",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",{"$f":"IF(T14<=8,0,IF(T14<=13,(ROUNDDOWN(T14,0)-8)*0.5,\"台数ｵｰﾊﾞ\"))","v":0},0,0,20,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ450HKXA     "," ",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",{"$f":"IF(T15<=8,0,IF(T15<=16,(ROUNDDOWN(T15,0)-8)*0.5,\"台数ｵｰﾊﾞ\"))","v":0},0,0,20,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ224HKX2A-K  "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCJ280HKX2A-K  "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCJ224HKX2A-KT "," ",null,null,null,null,5,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",{"$f":"IF(J18=\"φ6.4\",K18*L18,IF(J18=\"φ9.5\",K18*M18,IF(J18=\"φ12.7\",K18*N18,IF(J18=\"φ15.9\",K18*O18,IF(J18=\"φ19.1\",K18*P18,IF(J18=\"φ22.2\",K18*Q18,IF(J18=\"φ25.4\",K18*R18,0)))))))","v":0},null,"その他",0,0,0,5,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCJ280HKX2A-KT "," ",null,null,null,null,7,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,7,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCJ225HKX2A-KT "," ",null,null,null,null,5,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,5,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCJ281HKX2A-KT "," ",null,null,null,null,7,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,7,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCJ500HKX2A",null,"FDCJ280HKX2A-K  ","FDCJ224HKX2A-KT ",null,null,{"$f":"12+5","v":17},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ560HKX2A",null,"FDCJ280HKX2A-K  ","FDCJ280HKX2A-KT ",null,null,{"$f":"12+7","v":19},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,19,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ672HKX2A",null,"FDCJ224HKX2A-K  ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ728HKX2A",null,"FDCJ280HKX2A-K  ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ784HKX2A",null,"FDCJ280HKX2A-K  ","FDCJ224HKX2A-KT ","FDCJ280HKX2A-KT ",null,{"$f":"12+5+7","v":24},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,24,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ840HKX2A",null,"FDCJ280HKX2A-K  ","FDCJ280HKX2A-KT ","FDCJ280HKX2A-KT ",null,{"$f":"12+7+7","v":26},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,26,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ500HKX2AF",null,"FDCJ280HKX2A-K  ","FDCJ225HKX2A-KT ",null,null,{"$f":"12+5","v":17},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ560HKX2AF",null,"FDCJ280HKX2A-K  ","FDCJ281HKX2A-KT ",null,null,{"$f":"12+7","v":19},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,{"$f":"V29","v":0},{"$f":"IF(S29+W29<0,0,S29+W29)","v":0},19,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ672HKX2AF",null,"FDCJ224HKX2A-K  ","FDCJ225HKX2A-KT ","FDCJ225HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ728HKX2AF",null,"FDCJ280HKX2A-K  ","FDCJ225HKX2A-KT ","FDCJ224HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ784HKX2AF",null,"FDCJ280HKX2A-K  ","FDCJ225HKX2A-KT ","FDCJ281HKX2A-KT ",null,{"$f":"12+5+7","v":24},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,24,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ840HKX2AF",null,"FDCJ280HKX2A-K  ","FDCJ281HKX2A-KT ","FDCJ281HKX2A-KT ",null,{"$f":"12+7+7","v":26},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,26,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ224HKX2A-K "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCSJ280HKX2A-K "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCSJ224HKX2A-KT"," ",null,null,null,null,5,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,5,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCSJ280HKX2A-KT"," ",null,null,null,null,7,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,7,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCSJ225HKX2A-KT"," ",null,null,null,null,5,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,5,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCSJ281HKX2A-KT"," ",null,null,null,null,7,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,7,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCSJ500HKX2A",null,"FDCSJ280HKX2A-K  ","FDCSJ224HKX2A-KT ",null,null,{"$f":"12+5","v":17},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ560HKX2A",null,"FDCSJ280HKX2A-K  ","FDCSJ280HKX2A-KT ",null,null,{"$f":"12+7","v":19},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,19,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ672HKX2A",null,"FDCSJ224HKX2A-K  ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ728HKX2A",null,"FDCSJ280HKX2A-K  ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ784HKX2A",null,"FDCSJ280HKX2A-K  ","FDCSJ224HKX2A-KT ","FDCSJ280HKX2A-KT ",null,{"$f":"12+5+7","v":24},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,24,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ840HKX2A",null,"FDCSJ280HKX2A-K  ","FDCSJ280HKX2A-KT ","FDCSJ280HKX2A-KT ",null,{"$f":"12+7+7","v":26},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,26,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ500HKX2AF",null,"FDCSJ280HKX2A-K  ","FDCSJ225HKX2A-KT ",null,null,{"$f":"12+5","v":17},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ560HKX2AF",null,"FDCSJ280HKX2A-K  ","FDCSJ281HKX2A-KT ",null,null,{"$f":"12+7","v":19},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,19,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ672HKX2AF",null,"FDCSJ224HKX2A-K  ","FDCSJ225HKX2A-KT ","FDCSJ225HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ728HKX2AF",null,"FDCSJ280HKX2A-K  ","FDCSJ225HKX2A-KT ","FDCSJ224HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ784HKX2AF",null,"FDCSJ280HKX2A-K  ","FDCSJ225HKX2A-KT ","FDCSJ281HKX2A-KT ",null,{"$f":"12+5+7","v":24},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,24,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ840HKX2AF",null,"FDCSJ280HKX2A-K  ","FDCSJ281HKX2A-KT ","FDCSJ281HKX2A-KT ",null,{"$f":"12+7+7","v":26},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,26,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ224HKXRA    "," ",null,null,null,null,11,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,11,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ280HKXRA    "," ",null,null,null,null,11,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,11,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ560HKXRA    "," ",null,null,null,null,29,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",0,0,0,29,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ224HKXRA   "," ",null,null,null,null,11,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,11,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ280HKXRA   "," ",null,null,null,null,11,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,11,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ560HKXRA   "," ",null,null,null,null,29,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",0,0,0,29,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ224HKXRWA   "," ",null,null,null,null,11,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,11,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ280HKXRWA   "," ",null,null,null,null,11,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,11,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ224HMXA     "," ",null,null,null,null,11,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,11,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ280HMXA     "," ",null,null,null,null,11.4,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,11.4,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ224HMXA    "," ",null,null,null,null,11,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,11,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ280HMXA    "," ",null,null,null,null,11.4,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,11.4,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ224HMXA-K   "," ",null,null,null,null,11,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,11,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ280HMXA-K   "," ",null,null,null,null,11.4,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,11.4,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ224HMXA-K  "," ",null,null,null,null,11,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,11,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ280HMXA-K  "," ",null,null,null,null,11.4,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,11.4,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ450HMXA"," ","FDCJ224HMXA-K   ","FDCJ224HMXA-K   ",null,null,{"$f":"11+11","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ500HMXA"," ","FDCJ224HMXA-K   ","FDCJ280HMXA-K   ",null,null,{"$f":"11+11.4","v":22.4},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,22.4,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ560HMXA"," ","FDCJ280HMXA-K   ","FDCJ280HMXA-K   ",null,null,{"$f":"11.4+11.4","v":22.8},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,{"$f":"V70","v":0},{"$f":"IF(S70+W70<0,0,S70+W70)","v":0},{"$f":"H70+X70","v":22.8},{"$f":"Y70/I70","v":{"$error":"#DIV/0!"}},{"$f":"IF(A70=\"R410A\",0.39,IF(A70=\"R407C\",0.27,IF(A70=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A70=\"R410A\",0.42,IF(A70=\"R407C\",0.46,IF(A70=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(A70=\"R410A\",0.42,IF(A70=\"R407C\",0.49,IF(A70=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(OR(Z70<=AA70,AND(U70=\"その他\",Z70<=AB70)),\"OK\",IF(OR(AND(U70=\"最下層\",Z70<=AB70),AND(U70=\"その他\",Z70<=AC70)),\"対策が１つ必要です\",IF(OR(AND(U70=\"最下層\",Z70<=AC70),AND(U70=\"その他\",Z70>AC70)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R22","FDCJ672HMXA"," ","FDCJ224HMXA-K   ","FDCJ224HMXA-K   ","FDCJ224HMXA-K   ",null,{"$f":"11+11+11","v":33},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,33,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ728HMXA"," ","FDCJ224HMXA-K   ","FDCJ224HMXA-K   ","FDCJ280HMXA-K   ",null,{"$f":"11+11+11.4","v":33.4},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,33.4,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ784HMXA"," ","FDCJ224HMXA-K   ","FDCJ280HMXA-K   ","FDCJ280HMXA-K   ",null,{"$f":"11+11.4+11.4","v":33.799999999999997},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,33.799999999999997,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ840HMXA"," ","FDCJ280HMXA-K   ","FDCJ280HMXA-K   ","FDCJ280HMXA-K   ",null,{"$f":"11.4+11.4+11.4","v":34.200000000000003},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,34.200000000000003,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ450HMXA"," ","FDCSJ224HMXA-K  ","FDCSJ224HMXA-K  ",null,null,{"$f":"11+11","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ500HMXA"," ","FDCSJ224HMXA-K  ","FDCSJ280HMXA-K  ",null,null,{"$f":"11+11.4","v":22.4},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,22.4,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ560HMXA"," ","FDCSJ280HMXA-K  ","FDCSJ280HMXA-K  ",null,null,{"$f":"11.4+11.4","v":22.8},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,22.8,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ672HMXA"," ","FDCSJ224HMXA-K  ","FDCSJ224HMXA-K  ","FDCSJ224HMXA-K  ",null,{"$f":"11+11+11","v":33},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,33,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ728HMXA"," ","FDCSJ224HMXA-K  ","FDCSJ224HMXA-K  ","FDCSJ280HMXA-K  ",null,{"$f":"11+11+11.4","v":33.4},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,33.4,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ784HMXA"," ","FDCSJ224HMXA-K  ","FDCSJ280HMXA-K  ","FDCSJ280HMXA-K  ",null,{"$f":"11+11.4+11.4","v":33.799999999999997},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,33.799999999999997,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ840HMXA"," ","FDCSJ280HMXA-K  ","FDCSJ280HMXA-K  ","FDCSJ280HMXA-K  ",null,{"$f":"11.4+11.4+11.4","v":34.200000000000003},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,34.200000000000003,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ112HSXA     "," ",null,null,null,null,3.5,null,null,null,0.03,0.06,"***","***","***","***","***",{"$f":"IF(J82=\"φ6.4\",K82*L82,IF(J82=\"φ9.5\",K82*M82,IF(J82=\"φ12.7\",K82*N82,IF(J82=\"φ15.9\",K82*O82,IF(J82=\"φ19.1\",K82*P82,IF(J82=\"φ22.2\",K82*Q82,IF(J82=\"φ25.4\",K82*R82,0)))))))","v":0},null,"その他",0,0,0,3.5,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ140HSXA     "," ",null,null,null,null,3.5,null,null,null,0.03,0.06,"***","***","***","***","***",0,null,"その他",0,0,0,3.5,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ160HSXA     "," ",null,null,null,null,3.5,null,null,null,0.03,0.06,"***","***","***","***","***",0,null,"その他",0,0,0,3.5,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ112HSXA    "," ",null,null,null,null,3.5,null,null,null,0.03,0.06,"***","***","***","***","***",0,null,"その他",0,0,0,3.5,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ140HSXA    "," ",null,null,null,null,3.5,null,null,null,0.03,0.06,"***","***","***","***","***",0,null,"その他",0,0,0,3.5,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ160HSXA    "," ",null,null,null,null,3.5,null,null,null,0.03,0.06,"***","***","***","***","***",0,null,"その他",0,0,0,3.5,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R407C","FDCP140HKX2A    "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP160HKX2A    "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP224HKX2A    "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP280HKX2A    "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R22","FDCSJ140HKX2A   "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ160HKX2A   "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ224HKX2A   "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ280HKX2A   "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ355HKX2A   "," ",null,null,null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,{"$f":"IF(S96+W96<0,0,S96+W96)","v":0},16.350000000000001,{"$error":"#DIV/0!"},{"$f":"IF(A96=\"R410A\",0.39,IF(A96=\"R407C\",0.27,IF(A96=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A96=\"R410A\",0.42,IF(A96=\"R407C\",0.46,IF(A96=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ450HKX2A   "," ",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,{"$f":"IF(S97+W97<0,0,S97+W97)","v":0},20,{"$error":"#DIV/0!"},{"$f":"IF(A97=\"R410A\",0.39,IF(A97=\"R407C\",0.27,IF(A97=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A97=\"R410A\",0.42,IF(A97=\"R407C\",0.46,IF(A97=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ355HKXA    "," ",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",{"$f":"IF(T98<=8,0,IF(T98<=13,(ROUNDDOWN(T98,0)-8)*0.5,\"台数ｵｰﾊﾞ\"))","v":0},0,0,20,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ450HKXA    "," ",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",{"$f":"IF(T99<=8,0,IF(T99<=16,(ROUNDDOWN(T99,0)-8)*0.5,\"台数ｵｰﾊﾞ\"))","v":0},0,0,20,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ560HKXA    "," ",null,null,null,null,26,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",{"$f":"IF(T100<=8,0,IF(T100<=16,(ROUNDDOWN(T100,0)-8)*0.5,\"台数ｵｰﾊﾞ\"))","v":0},0,0,26,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ672HKXA    "," ",null,null,null,null,26,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",0,0,0,26,{"$error":"#DIV/0!"},{"$f":"IF(A101=\"R410A\",0.39,IF(A101=\"R407C\",0.27,IF(A101=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A101=\"R410A\",0.42,IF(A101=\"R407C\",0.46,IF(A101=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ728HKXA    "," ",null,null,null,null,40,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,40,{"$error":"#DIV/0!"},{"$f":"IF(A102=\"R410A\",0.39,IF(A102=\"R407C\",0.27,IF(A102=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A102=\"R410A\",0.42,IF(A102=\"R407C\",0.46,IF(A102=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ784HKXA    "," ",null,null,null,null,40,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,40,{"$error":"#DIV/0!"},{"$f":"IF(A103=\"R410A\",0.39,IF(A103=\"R407C\",0.27,IF(A103=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A103=\"R410A\",0.42,IF(A103=\"R407C\",0.46,IF(A103=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ840HKXA    "," ",null,null,null,null,40,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,40,{"$error":"#DIV/0!"},{"$f":"IF(A104=\"R410A\",0.39,IF(A104=\"R407C\",0.27,IF(A104=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A104=\"R410A\",0.42,IF(A104=\"R407C\",0.46,IF(A104=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ560HKXA     "," ",null,null,null,null,26,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",{"$f":"IF(T105<=8,0,IF(T105<=16,(ROUNDDOWN(T105,0)-8)*0.5,\"台数ｵｰﾊﾞ\"))","v":0},0,0,26,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ672HKXA     "," ",null,null,null,null,26,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",0,0,0,26,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ728HKXA     "," ",null,null,null,null,40,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,40,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ784HKXA     "," ",null,null,null,null,40,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,40,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ840HKXA     "," ",null,null,null,null,40,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,"***",0,null,"その他",0,0,0,40,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ355HKX2A    "," ",null,null,null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,16.350000000000001,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ450HKX2A    "," ",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,20,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ140HKX2A    ","A",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ160HKX2A    ","A",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ224HKX2A    ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ280HKX2A    ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R407C","FDCP140HKX2A    ","A",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP160HKX2A    ","A",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP224HKX2A    ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP280HKX2A    ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP355HKX2A    "," ",null,null,null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,16.350000000000001,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP450HKX2A    "," ",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,20,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R22","FDCJ224HKX2B-K  "," ",null,null,null,null,12,null,null,50,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCJ280HKX2B-K  "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCSJ224HKX2B-K "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCSJ280HKX2B-K "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCP224HKX2B-K  "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCP280HKX2B-K  "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCP224HKX2A-KT "," ",null,null,null,null,5,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,5,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCP280HKX2A-KT "," ",null,null,null,null,7,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,7,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCP225HKX2A-KT "," ",null,null,null,null,5,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,5,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCP281HKX2A-KT "," ",null,null,null,null,7,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,7,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCSP224HKX2B-K "," ",null,null,null,null,5,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,5,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCSP280HKX2B-K "," ",null,null,null,null,7,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,{"$f":"V133","v":0},{"$f":"IF(S133+W133<0,0,S133+W133)","v":0},7,{"$error":"#DIV/0!"},{"$f":"IF(A133=\"R410A\",0.39,IF(A133=\"R407C\",0.27,IF(A133=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(A133=\"R410A\",0.42,IF(A133=\"R407C\",0.46,IF(A133=\"R22\",0.28,\"NG\")))","v":0.46},{"$f":"IF(A133=\"R410A\",0.42,IF(A133=\"R407C\",0.49,IF(A133=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(OR(Z133<=AA133,AND(U133=\"その他\",Z133<=AB133)),\"OK\",IF(OR(AND(U133=\"最下層\",Z133<=AB133),AND(U133=\"その他\",Z133<=AC133)),\"対策が１つ必要です\",IF(OR(AND(U133=\"最下層\",Z133<=AC133),AND(U133=\"その他\",Z133>AC133)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}},"組合せ専用機"]
["R407C","FDCSP224HKX2A-KT"," ",null,null,null,null,5,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,{"$f":"H134+X134","v":5},{"$f":"Y134/I134","v":{"$error":"#DIV/0!"}},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCSP280HKX2A-KT"," ",null,null,null,null,7,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,7,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCSP281HKX2A-KT"," ",null,null,null,null,5,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,5,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCSP225HKX2A-KT"," ",null,null,null,null,7,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,7,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCJ140HKX2B    "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ160HKX2B    "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ224HKX2B    "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ280HKX2B    "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ140HKX2B   "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ160HKX2B   "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ224HKX2B   "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ280HKX2B   "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R407C","FDCP140HKX2B    "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",{"$f":"IF(J146=\"φ6.4\",K146*L146,IF(J146=\"φ9.5\",K146*M146,IF(J146=\"φ12.7\",K146*N146,IF(J146=\"φ15.9\",K146*O146,IF(J146=\"φ19.1\",K146*P146,IF(J146=\"φ22.2\",K146*Q146,IF(J146=\"φ25.4\",K146*R146,0)))))))","v":0},null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP160HKX2B    "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP224HKX2B    "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP280HKX2B    "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP140HKX2B   "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.27,0.46,{"$f":"IF(A150=\"R410A\",0.42,IF(A150=\"R407C\",0.49,IF(A150=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(OR(Z150<=AA150,AND(U150=\"その他\",Z150<=AB150)),\"OK\",IF(OR(AND(U150=\"最下層\",Z150<=AB150),AND(U150=\"その他\",Z150<=AC150)),\"対策が１つ必要です\",IF(OR(AND(U150=\"最下層\",Z150<=AC150),AND(U150=\"その他\",Z150>AC150)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R407C","FDCSP160HKX2B   "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.27,0.46,{"$f":"IF(A151=\"R410A\",0.42,IF(A151=\"R407C\",0.49,IF(A151=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(OR(Z151<=AA151,AND(U151=\"その他\",Z151<=AB151)),\"OK\",IF(OR(AND(U151=\"最下層\",Z151<=AB151),AND(U151=\"その他\",Z151<=AC151)),\"対策が１つ必要です\",IF(OR(AND(U151=\"最下層\",Z151<=AC151),AND(U151=\"その他\",Z151>AC151)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R407C","FDCSP224HKX2B   "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,{"$f":"IF(A152=\"R410A\",0.42,IF(A152=\"R407C\",0.49,IF(A152=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(OR(Z152<=AA152,AND(U152=\"その他\",Z152<=AB152)),\"OK\",IF(OR(AND(U152=\"最下層\",Z152<=AB152),AND(U152=\"その他\",Z152<=AC152)),\"対策が１つ必要です\",IF(OR(AND(U152=\"最下層\",Z152<=AC152),AND(U152=\"その他\",Z152>AC152)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R407C","FDCSP280HKX2B   "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,{"$f":"IF(A153=\"R410A\",0.42,IF(A153=\"R407C\",0.49,IF(A153=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(OR(Z153<=AA153,AND(U153=\"その他\",Z153<=AB153)),\"OK\",IF(OR(AND(U153=\"最下層\",Z153<=AB153),AND(U153=\"その他\",Z153<=AC153)),\"対策が１つ必要です\",IF(OR(AND(U153=\"最下層\",Z153<=AC153),AND(U153=\"その他\",Z153>AC153)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R22","FDCSJ224HKXIB   "," ","ISU10HKX","FDCSJ224HKXIB   ",null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",1.2,1.2,1.2,13.2,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ280HKXIB   "," ","ISU13HKX","FDCSJ280HKXIB   ",null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",2.2000000000000002,2.2000000000000002,2.2000000000000002,14.2,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R407C","FDCSP355HKX2A   "," ",null,null,null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,16.350000000000001,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP450HKX2A   "," ",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,{"$f":"V157","v":0},0,20,{"$error":"#DIV/0!"},0.27,0.46,{"$f":"IF(A157=\"R410A\",0.42,IF(A157=\"R407C\",0.49,IF(A157=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(OR(Z157<=AA157,AND(U157=\"その他\",Z157<=AB157)),\"OK\",IF(OR(AND(U157=\"最下層\",Z157<=AB157),AND(U157=\"その他\",Z157<=AC157)),\"対策が１つ必要です\",IF(OR(AND(U157=\"最下層\",Z157<=AC157),AND(U157=\"その他\",Z157>AC157)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R407C","FDCSP140HKX2B-C "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R22","FDCJ224HKX2D    "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,{"$f":"V159","v":0},0,12,{"$error":"#DIV/0!"},{"$f":"IF(A159=\"R410A\",0.39,IF(A159=\"R407C\",0.27,IF(A159=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A159=\"R410A\",0.42,IF(A159=\"R407C\",0.46,IF(A159=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(A159=\"R410A\",0.42,IF(A159=\"R407C\",0.49,IF(A159=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(OR(Z159<=AA159,AND(U159=\"その他\",Z159<=AB159)),\"OK\",IF(OR(AND(U159=\"最下層\",Z159<=AB159),AND(U159=\"その他\",Z159<=AC159)),\"対策が１つ必要です\",IF(OR(AND(U159=\"最下層\",Z159<=AC159),AND(U159=\"その他\",Z159>AC159)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R22","FDCJ280HKX2D    "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,{"$f":"V160","v":0},0,12,{"$error":"#DIV/0!"},{"$f":"IF(A160=\"R410A\",0.39,IF(A160=\"R407C\",0.27,IF(A160=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A160=\"R410A\",0.42,IF(A160=\"R407C\",0.46,IF(A160=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(A160=\"R410A\",0.42,IF(A160=\"R407C\",0.49,IF(A160=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(OR(Z160<=AA160,AND(U160=\"その他\",Z160<=AB160)),\"OK\",IF(OR(AND(U160=\"最下層\",Z160<=AB160),AND(U160=\"その他\",Z160<=AC160)),\"対策が１つ必要です\",IF(OR(AND(U160=\"最下層\",Z160<=AC160),AND(U160=\"その他\",Z160>AC160)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R22","FDCJ355HKX2D    "," ",null,null,null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,16.350000000000001,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ450HKX2D    "," ",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,20,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R407C","FDCP355HKX2D    "," ",null,null,null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,16.350000000000001,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP450HKX2D    "," ",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,{"$f":"V164","v":0},0,20,{"$error":"#DIV/0!"},{"$f":"IF(A164=\"R410A\",0.39,IF(A164=\"R407C\",0.27,IF(A164=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(A164=\"R410A\",0.42,IF(A164=\"R407C\",0.46,IF(A164=\"R22\",0.28,\"NG\")))","v":0.46},{"$f":"IF(A164=\"R410A\",0.42,IF(A164=\"R407C\",0.49,IF(A164=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(OR(Z164<=AA164,AND(U164=\"その他\",Z164<=AB164)),\"OK\",IF(OR(AND(U164=\"最下層\",Z164<=AB164),AND(U164=\"その他\",Z164<=AC164)),\"対策が１つ必要です\",IF(OR(AND(U164=\"最下層\",Z164<=AC164),AND(U164=\"その他\",Z164>AC164)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R22","FDCJ224HKX2D-K  "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCJ280HKX2D-K  "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCSJ224HKX2D-K "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,{"$f":"V167","v":0},{"$f":"IF(S167+W167<0,0,S167+W167)","v":0},12,{"$error":"#DIV/0!"},{"$f":"IF(A167=\"R410A\",0.39,IF(A167=\"R407C\",0.27,IF(A167=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A167=\"R410A\",0.42,IF(A167=\"R407C\",0.46,IF(A167=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(A167=\"R410A\",0.42,IF(A167=\"R407C\",0.49,IF(A167=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(OR(Z167<=AA167,AND(U167=\"その他\",Z167<=AB167)),\"OK\",IF(OR(AND(U167=\"最下層\",Z167<=AB167),AND(U167=\"その他\",Z167<=AC167)),\"対策が１つ必要です\",IF(OR(AND(U167=\"最下層\",Z167<=AC167),AND(U167=\"その他\",Z167>AC167)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}},"組合せ専用機"]
["R22","FDCSJ280HKX2D-K "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,{"$f":"V168","v":0},{"$f":"IF(S168+W168<0,0,S168+W168)","v":0},12,{"$error":"#DIV/0!"},{"$f":"IF(A168=\"R410A\",0.39,IF(A168=\"R407C\",0.27,IF(A168=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A168=\"R410A\",0.42,IF(A168=\"R407C\",0.46,IF(A168=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(A168=\"R410A\",0.42,IF(A168=\"R407C\",0.49,IF(A168=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(OR(Z168<=AA168,AND(U168=\"その他\",Z168<=AB168)),\"OK\",IF(OR(AND(U168=\"最下層\",Z168<=AB168),AND(U168=\"その他\",Z168<=AC168)),\"対策が１つ必要です\",IF(OR(AND(U168=\"最下層\",Z168<=AC168),AND(U168=\"その他\",Z168>AC168)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}},"組合せ専用機"]
["R407C","FDCP224HKX2D-K  "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCP280HKX2D-K  "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCSP224HKX2D-K "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,{"$f":"V171","v":0},{"$f":"IF(S171+W171<0,0,S171+W171)","v":0},12,{"$error":"#DIV/0!"},{"$f":"IF(A171=\"R410A\",0.39,IF(A171=\"R407C\",0.27,IF(A171=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(A171=\"R410A\",0.42,IF(A171=\"R407C\",0.46,IF(A171=\"R22\",0.28,\"NG\")))","v":0.46},{"$f":"IF(A171=\"R410A\",0.42,IF(A171=\"R407C\",0.49,IF(A171=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(OR(Z171<=AA171,AND(U171=\"その他\",Z171<=AB171)),\"OK\",IF(OR(AND(U171=\"最下層\",Z171<=AB171),AND(U171=\"その他\",Z171<=AC171)),\"対策が１つ必要です\",IF(OR(AND(U171=\"最下層\",Z171<=AC171),AND(U171=\"その他\",Z171>AC171)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}},"組合せ専用機"]
["R407C","FDCSP280HKX2D-K "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,{"$f":"V172","v":0},{"$f":"IF(S172+W172<0,0,S172+W172)","v":0},12,{"$error":"#DIV/0!"},{"$f":"IF(A172=\"R410A\",0.39,IF(A172=\"R407C\",0.27,IF(A172=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(A172=\"R410A\",0.42,IF(A172=\"R407C\",0.46,IF(A172=\"R22\",0.28,\"NG\")))","v":0.46},{"$f":"IF(A172=\"R410A\",0.42,IF(A172=\"R407C\",0.49,IF(A172=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(OR(Z172<=AA172,AND(U172=\"その他\",Z172<=AB172)),\"OK\",IF(OR(AND(U172=\"最下層\",Z172<=AB172),AND(U172=\"その他\",Z172<=AC172)),\"対策が１つ必要です\",IF(OR(AND(U172=\"最下層\",Z172<=AC172),AND(U172=\"その他\",Z172>AC172)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}},"組合せ専用機"]
["R22","FDCSJ224HKX2D   "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ280HKX2D   "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,{"$f":"V174","v":0},{"$f":"IF(S174+W174<0,0,S174+W174)","v":0},12,{"$error":"#DIV/0!"},{"$f":"IF(A174=\"R410A\",0.39,IF(A174=\"R407C\",0.27,IF(A174=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A174=\"R410A\",0.42,IF(A174=\"R407C\",0.46,IF(A174=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(A174=\"R410A\",0.42,IF(A174=\"R407C\",0.49,IF(A174=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(OR(Z174<=AA174,AND(U174=\"その他\",Z174<=AB174)),\"OK\",IF(OR(AND(U174=\"最下層\",Z174<=AB174),AND(U174=\"その他\",Z174<=AC174)),\"対策が１つ必要です\",IF(OR(AND(U174=\"最下層\",Z174<=AC174),AND(U174=\"その他\",Z174>AC174)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R22","FDCSJ355HKX2D   "," ",null,null,null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,16.350000000000001,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ450HKX2D   "," ",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,20,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R407C","FDCSP355HKX2D   "," ",null,null,null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,16.350000000000001,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP450HKX2D   "," ",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,20,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP224HKX2D    "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP280HKX2D    "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP224HKX2D   "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP280HKX2D   "," ",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,{"$f":"V182","v":0},{"$f":"IF(S182+W182<0,0,S182+W182)","v":0},12,{"$error":"#DIV/0!"},{"$f":"IF(A182=\"R410A\",0.39,IF(A182=\"R407C\",0.27,IF(A182=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(A182=\"R410A\",0.42,IF(A182=\"R407C\",0.46,IF(A182=\"R22\",0.28,\"NG\")))","v":0.46},{"$f":"IF(A182=\"R410A\",0.42,IF(A182=\"R407C\",0.49,IF(A182=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(OR(Z182<=AA182,AND(U182=\"その他\",Z182<=AB182)),\"OK\",IF(OR(AND(U182=\"最下層\",Z182<=AB182),AND(U182=\"その他\",Z182<=AC182)),\"対策が１つ必要です\",IF(OR(AND(U182=\"最下層\",Z182<=AC182),AND(U182=\"その他\",Z182>AC182)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R22","FDCJ140HKX2D    "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ160HKX2D    "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ140HKX2D   "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,{"$f":"V185","v":0},{"$f":"IF(S185+W185<0,0,S185+W185)","v":0},9,{"$error":"#DIV/0!"},{"$f":"IF(A185=\"R410A\",0.39,IF(A185=\"R407C\",0.27,IF(A185=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A185=\"R410A\",0.42,IF(A185=\"R407C\",0.46,IF(A185=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(A185=\"R410A\",0.42,IF(A185=\"R407C\",0.49,IF(A185=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(OR(Z185<=AA185,AND(U185=\"その他\",Z185<=AB185)),\"OK\",IF(OR(AND(U185=\"最下層\",Z185<=AB185),AND(U185=\"その他\",Z185<=AC185)),\"対策が１つ必要です\",IF(OR(AND(U185=\"最下層\",Z185<=AC185),AND(U185=\"その他\",Z185>AC185)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R22","FDCSJ160HKX2D   "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,{"$f":"V186","v":0},{"$f":"IF(S186+W186<0,0,S186+W186)","v":0},9,{"$error":"#DIV/0!"},{"$f":"IF(A186=\"R410A\",0.39,IF(A186=\"R407C\",0.27,IF(A186=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A186=\"R410A\",0.42,IF(A186=\"R407C\",0.46,IF(A186=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(A186=\"R410A\",0.42,IF(A186=\"R407C\",0.49,IF(A186=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(OR(Z186<=AA186,AND(U186=\"その他\",Z186<=AB186)),\"OK\",IF(OR(AND(U186=\"最下層\",Z186<=AB186),AND(U186=\"その他\",Z186<=AC186)),\"対策が１つ必要です\",IF(OR(AND(U186=\"最下層\",Z186<=AC186),AND(U186=\"その他\",Z186>AC186)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R407C","FDCP140HKX2D    "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP160HKX2D    "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP140HKX2D   "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP160HKX2D   "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP224HKXRA    "," ",null,null,null,null,11,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,11,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP280HKXRA    "," ",null,null,null,null,11,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,11,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP560HKXRA    "," ",null,null,null,null,29,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",0,0,0,29,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP560HKXRA    ","A",null,null,null,null,29,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",0,0,0,29,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP224HKXRA   "," ",null,null,null,null,11,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,11,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP280HKXRA   "," ",null,null,null,null,11,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,11,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP560HKXRA   "," ",null,null,null,null,29,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",0,{"$f":"V197","v":0},{"$f":"IF(S197+W197<0,0,S197+W197)","v":0},29,{"$error":"#DIV/0!"},{"$f":"IF(A197=\"R410A\",0.39,IF(A197=\"R407C\",0.27,IF(A197=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(A197=\"R410A\",0.42,IF(A197=\"R407C\",0.46,IF(A197=\"R22\",0.28,\"NG\")))","v":0.46},{"$f":"IF(A197=\"R410A\",0.42,IF(A197=\"R407C\",0.49,IF(A197=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(OR(Z197<=AA197,AND(U197=\"その他\",Z197<=AB197)),\"OK\",IF(OR(AND(U197=\"最下層\",Z197<=AB197),AND(U197=\"その他\",Z197<=AC197)),\"対策が１つ必要です\",IF(OR(AND(U197=\"最下層\",Z197<=AC197),AND(U197=\"その他\",Z197>AC197)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R22","FDCJ355HKXIS1   "," ","ISUJ450HS1","FDCJ355HKXIS1   ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",26,{"$f":"V198","v":26},{"$f":"IF(S198+W198<0,0,S198+W198)","v":26},{"$f":"H198+X198","v":46},{"$f":"Y198/I198","v":{"$error":"#DIV/0!"}},{"$f":"IF(A198=\"R410A\",0.39,IF(A198=\"R407C\",0.27,IF(A198=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A198=\"R410A\",0.42,IF(A198=\"R407C\",0.46,IF(A198=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ450HKXIS1   "," ","ISUJ560HS1","FDCJ450HKXIS1   ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",26,{"$f":"V199","v":26},{"$f":"IF(S199+W199<0,0,S199+W199)","v":26},46,{"$error":"#DIV/0!"},{"$f":"IF(A199=\"R410A\",0.39,IF(A199=\"R407C\",0.27,IF(A199=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A199=\"R410A\",0.42,IF(A199=\"R407C\",0.46,IF(A199=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ280HKXIS1A  "," ","ISUJ355HS1","FDCJ280HKXIS1A  ",null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",17,{"$f":"V200","v":17},{"$f":"IF(S200+W200<0,0,S200+W200)","v":17},33.35,{"$error":"#DIV/0!"},{"$f":"IF(A200=\"R410A\",0.39,IF(A200=\"R407C\",0.27,IF(A200=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A200=\"R410A\",0.42,IF(A200=\"R407C\",0.46,IF(A200=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ355HKXIS1A  "," ","ISUJ450HS1","FDCJ355HKXIS1A  ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",26,26,26,46,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ450HKXIS1A  "," ","ISUJ560HS1","FDCJ450HKXIS1A  ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",26,26,26,46,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ280HKXIS1A  ","B","ISUJ355HS1","FDCJ280HKXIS1A  ",null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",17,{"$f":"V203","v":17},{"$f":"IF(S203+W203<0,0,S203+W203)","v":17},33.35,{"$error":"#DIV/0!"},{"$f":"IF(A203=\"R410A\",0.39,IF(A203=\"R407C\",0.27,IF(A203=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A203=\"R410A\",0.42,IF(A203=\"R407C\",0.46,IF(A203=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(A203=\"R410A\",0.42,IF(A203=\"R407C\",0.49,IF(A203=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(OR(Z203<=AA203,AND(U203=\"その他\",Z203<=AB203)),\"OK\",IF(OR(AND(U203=\"最下層\",Z203<=AB203),AND(U203=\"その他\",Z203<=AC203)),\"対策が１つ必要です\",IF(OR(AND(U203=\"最下層\",Z203<=AC203),AND(U203=\"その他\",Z203>AC203)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R22","FDCJ355HKXIS1A  ","B","ISUJ450HS1","FDCJ355HKXIS1A  ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",26,{"$f":"V204","v":26},{"$f":"IF(S204+W204<0,0,S204+W204)","v":26},46,{"$error":"#DIV/0!"},{"$f":"IF(A204=\"R410A\",0.39,IF(A204=\"R407C\",0.27,IF(A204=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A204=\"R410A\",0.42,IF(A204=\"R407C\",0.46,IF(A204=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(A204=\"R410A\",0.42,IF(A204=\"R407C\",0.49,IF(A204=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(OR(Z204<=AA204,AND(U204=\"その他\",Z204<=AB204)),\"OK\",IF(OR(AND(U204=\"最下層\",Z204<=AB204),AND(U204=\"その他\",Z204<=AC204)),\"対策が１つ必要です\",IF(OR(AND(U204=\"最下層\",Z204<=AC204),AND(U204=\"その他\",Z204>AC204)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R22","FDCJ450HKXIS1A  ","B","ISUJ560HS1","FDCJ450HKXIS1A  ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",26,{"$f":"V205","v":26},{"$f":"IF(S205+W205<0,0,S205+W205)","v":26},46,{"$error":"#DIV/0!"},{"$f":"IF(A205=\"R410A\",0.39,IF(A205=\"R407C\",0.27,IF(A205=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A205=\"R410A\",0.42,IF(A205=\"R407C\",0.46,IF(A205=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(A205=\"R410A\",0.42,IF(A205=\"R407C\",0.49,IF(A205=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(OR(Z205<=AA205,AND(U205=\"その他\",Z205<=AB205)),\"OK\",IF(OR(AND(U205=\"最下層\",Z205<=AB205),AND(U205=\"その他\",Z205<=AC205)),\"対策が１つ必要です\",IF(OR(AND(U205=\"最下層\",Z205<=AC205),AND(U205=\"その他\",Z205>AC205)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R22","FDCSJ280HKXIS1A "," ","ISUSJ355HS1","FDCSJ280HKXIS1A ",null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",17,{"$f":"V206","v":17},{"$f":"IF(S206+W206<0,0,S206+W206)","v":17},33.35,{"$error":"#DIV/0!"},{"$f":"IF(A206=\"R410A\",0.39,IF(A206=\"R407C\",0.27,IF(A206=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A206=\"R410A\",0.42,IF(A206=\"R407C\",0.46,IF(A206=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(A206=\"R410A\",0.42,IF(A206=\"R407C\",0.49,IF(A206=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(OR(Z206<=AA206,AND(U206=\"その他\",Z206<=AB206)),\"OK\",IF(OR(AND(U206=\"最下層\",Z206<=AB206),AND(U206=\"その他\",Z206<=AC206)),\"対策が１つ必要です\",IF(OR(AND(U206=\"最下層\",Z206<=AC206),AND(U206=\"その他\",Z206>AC206)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R407C","FDCP280HKXIS1A  "," ","ISUP355HS1","FDCP280HKXIS1A  ",null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",17,17,17,33.35,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP355HKXIS1A  "," ","ISUP450HS1","FDCP355HKXIS1A  ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",26,26,26,46,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP450HKXIS1A  "," ","ISUP560HS1","FDCP450HKXIS1A  ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",26,26,26,46,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP280HKXIC1   "," ","ISUP355HC1","FDCP280HKXIC1   ",null,null,20,null,null,null,0.03,0.06,0.12,"***","***","***","***",{"$f":"IF(J210=\"φ6.4\",K210*L210,IF(J210=\"φ9.5\",K210*M210,IF(J210=\"φ12.7\",K210*N210,IF(J210=\"φ15.9\",K210*O210,IF(J210=\"φ19.1\",K210*P210,IF(J210=\"φ22.2\",K210*Q210,IF(J210=\"φ25.4\",K210*R210,0)))))))","v":0},null,"その他",19,19,19,39,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP355HKXIC1   "," ","ISUP450HC1","FDCP355HKXIC1   ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",22,22,22,42,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP280HKXIS1A "," ","ISUSP355HS1","FDCSP280HKXIS1A ",null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",17,17,17,33.35,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP355HKXIS1A "," ","ISUSP450HS1","FDCSP355HKXIS1A ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",26,26,26,46,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP450HKXIS1A "," ","ISUSP560HS1","FDCSP450HKXIS1A ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",26,26,26,46,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R22","FDCJ160HKX2D    ","A",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,{"$f":"V215","v":0},{"$f":"IF(S215+W215<0,0,S215+W215)","v":0},9,{"$error":"#DIV/0!"},{"$f":"IF(A215=\"R410A\",0.39,IF(A215=\"R407C\",0.27,IF(A215=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A215=\"R410A\",0.42,IF(A215=\"R407C\",0.46,IF(A215=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ224HKX2D    ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ280HKX2D    ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,{"$f":"IF(S217+W217<0,0,S217+W217)","v":0},12,{"$error":"#DIV/0!"},{"$f":"IF(A217=\"R410A\",0.39,IF(A217=\"R407C\",0.27,IF(A217=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A217=\"R410A\",0.42,IF(A217=\"R407C\",0.46,IF(A217=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ355HKX2D    ","A",null,null,null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,16.350000000000001,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ450HKX2D    ","A",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,20,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ224HKX2D   ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ280HKX2D   ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ355HKX2D   ","A",null,null,null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,16.350000000000001,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ450HKX2D   ","A",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,20,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ224HKX2D-K  ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCJ280HKX2D-K  ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCSJ224HKX2D-K ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCSJ280HKX2D-K ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCP224HKX2D    ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP280HKX2D    ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,{"$f":"IF(S229+W229<0,0,S229+W229)","v":0},12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP355HKX2D    ","A",null,null,null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,16.350000000000001,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP450HKX2D    ","A",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,20,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP224HKX2D   ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP280HKX2D   ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP355HKX2D   ","A",null,null,null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,16.350000000000001,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP450HKX2D   ","A",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,20,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP224HKX2D-K  ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCP280HKX2D-K  ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCSP224HKX2D-K ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCSP280HKX2D-K ","A",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCJ224HKX2D    ","B",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ280HKX2D    ","B",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ355HKX2D    ","B",null,null,null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,16.350000000000001,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ450HKX2D    ","B",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,20,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ224HKX2D   ","B",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ280HKX2D   ","B",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ355HKX2D   ","B",null,null,null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,16.350000000000001,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ450HKX2D   ","B",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,20,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ224HKX2D-K  ","B",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCJ280HKX2D-K  ","B",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCSJ224HKX2D-K ","B",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCSJ280HKX2D-K ","B",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"},"組合せ専用機"]
["R22","FDCJ500HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ224HKX2A-KT ",null,null,{"$f":"12+5","v":17},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ560HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ280HKX2A-KT ",null,null,{"$f":"12+7","v":19},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,19,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ672HKX2DA  ",null,"FDCJ224HKX2D-K  ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ728HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ784HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ224HKX2A-KT ","FDCJ280HKX2A-KT ",null,{"$f":"12+5+7","v":24},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,24,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ840HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ280HKX2A-KT ","FDCJ280HKX2A-KT ",null,{"$f":"12+7+7","v":26},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,26,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ896HKX2DA  ",null,"FDCJ224HKX2D-K  ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ",{"$f":"12+5+5+5","v":27},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,27,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ952HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ",{"$f":"12+5+5+5","v":27},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,27,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ1008HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ224HKX2A-KT ","FDCJ224HKX2A-KT ","FDCJ280HKX2A-KT ",{"$f":"12+5+5+7","v":29},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,29,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ1064HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ224HKX2A-KT ","FDCJ280HKX2A-KT ","FDCJ280HKX2A-KT ",{"$f":"12+5+7+7","v":31},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,{"$f":"V261","v":0},{"$f":"IF(S261+W261<0,0,S261+W261)","v":0},31,{"$error":"#DIV/0!"},{"$f":"IF(A261=\"R410A\",0.39,IF(A261=\"R407C\",0.27,IF(A261=\"R22\",0.21,\"NG\")))","v":0.21},{"$f":"IF(A261=\"R410A\",0.42,IF(A261=\"R407C\",0.46,IF(A261=\"R22\",0.28,\"NG\")))","v":0.28000000000000003},{"$f":"IF(A261=\"R410A\",0.42,IF(A261=\"R407C\",0.49,IF(A261=\"R22\",0.5,\"NG\")))","v":0.5},{"$f":"IF(OR(Z261<=AA261,AND(U261=\"その他\",Z261<=AB261)),\"OK\",IF(OR(AND(U261=\"最下層\",Z261<=AB261),AND(U261=\"その他\",Z261<=AC261)),\"対策が１つ必要です\",IF(OR(AND(U261=\"最下層\",Z261<=AC261),AND(U261=\"その他\",Z261>AC261)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R22","FDCJ1120HKX2DA  ",null,"FDCJ280HKX2D-K  ","FDCJ280HKX2A-KT ","FDCJ280HKX2A-KT ","FDCJ280HKX2A-KT ",{"$f":"12+7+7+7","v":33},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,{"$f":"H262+X262","v":33},{"$f":"Y262/I262","v":{"$error":"#DIV/0!"}},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ500HKX2DAF ",null,"FDCJ280HKX2D-K  ","FDCJ225HKX2A-KT ",null,null,{"$f":"12+5","v":17},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ560HKX2DAF  ",null,"FDCJ280HKX2D-K  ","FDCJ281HKX2A-KT ",null,null,{"$f":"12+7","v":19},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,19,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ672HKX2DAF  ",null,"FDCJ224HKX2D-K  ","FDCJ225HKX2A-KT ","FDCJ225HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ728HKX2DAF  ",null,"FDCJ280HKX2D-K  ","FDCJ225HKX2A-KT ","FDCJ225HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ784HKX2DAF  ",null,"FDCJ280HKX2D-K  ","FDCJ225HKX2A-KT ","FDCJ281HKX2A-KT ",null,{"$f":"12+5+7","v":24},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,24,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ840HKX2DAF  ",null,"FDCJ280HKX2D-K  ","FDCJ281HKX2A-KT ","FDCJ281HKX2A-KT ",null,{"$f":"12+7+7","v":26},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,26,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ896HKX2DAF  ",null,"FDCJ224HKX2D-K  ","FDCJ225HKX2A-KT ","FDCJ225HKX2A-KT ","FDCJ225HKX2A-KT ",{"$f":"12+5+5+5","v":27},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,27,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ952HKX2DAF  ",null,"FDCJ280HKX2D-K  ","FDCJ225HKX2A-KT ","FDCJ225HKX2A-KT ","FDCJ225HKX2A-KT ",{"$f":"12+5+5+5","v":27},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,27,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ1008HKX2DAF  ",null,"FDCJ280HKX2D-K  ","FDCJ225HKX2A-KT ","FDCJ225HKX2A-KT ","FDCJ281HKX2A-KT ",{"$f":"12+5+5+7","v":29},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,29,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ1064HKX2DAF  ",null,"FDCJ280HKX2D-K  ","FDCJ225HKX2A-KT ","FDCJ281HKX2A-KT ","FDCJ281HKX2A-KT ",{"$f":"12+5+7+7","v":31},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,31,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCJ1120HKX2DAF  ",null,"FDCJ280HKX2D-K  ","FDCJ281HKX2A-KT ","FDCJ281HKX2A-KT ","FDCJ281HKX2A-KT ",{"$f":"12+7+7+7","v":33},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,33,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ500HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ224HKX2A-KT ",null,null,{"$f":"12+5","v":17},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,{"$f":"IF(J274=\"φ6.4\",K274*L274,IF(J274=\"φ9.5\",K274*M274,IF(J274=\"φ12.7\",K274*N274,IF(J274=\"φ15.9\",K274*O274,IF(J274=\"φ19.1\",K274*P274,IF(J274=\"φ22.2\",K274*Q274,IF(J274=\"φ25.4\",K274*R274,0)))))))","v":0},null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ560HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ280HKX2A-KT ",null,null,{"$f":"12+7","v":19},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,19,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ672HKX2DA  ",null,"FDCSJ224HKX2D-K  ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ728HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ784HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ224HKX2A-KT ","FDCSJ280HKX2A-KT ",null,{"$f":"12+5+7","v":24},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,24,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ840HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ280HKX2A-KT ","FDCSJ280HKX2A-KT ",null,{"$f":"12+7+7","v":26},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,26,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ896HKX2DA  ",null,"FDCSJ224HKX2D-K  ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ",{"$f":"12+5+5+5","v":27},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,27,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ952HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ",{"$f":"12+5+5+5","v":27},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,27,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ1008HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ224HKX2A-KT ","FDCSJ224HKX2A-KT ","FDCSJ280HKX2A-KT ",{"$f":"12+5+5+7","v":29},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,29,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ1064HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ224HKX2A-KT ","FDCSJ280HKX2A-KT ","FDCSJ280HKX2A-KT ",{"$f":"12+5+7+7","v":31},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,31,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ1120HKX2DA  ",null,"FDCSJ280HKX2D-K  ","FDCSJ280HKX2A-KT ","FDCSJ280HKX2A-KT ","FDCSJ280HKX2A-KT ",{"$f":"12+7+7+7","v":33},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,33,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ500HKX2DAF ",null,"FDCSJ280HKX2D-K  ","FDCSJ225HKX2A-KT ",null,null,{"$f":"12+5","v":17},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ560HKX2DAF  ",null,"FDCSJ280HKX2D-K  ","FDCSJ281HKX2A-KT ",null,null,{"$f":"12+7","v":19},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,19,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ672HKX2DAF  ",null,"FDCSJ224HKX2D-K  ","FDCSJ225HKX2A-KT ","FDCSJ225HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ728HKX2DAF  ",null,"FDCSJ280HKX2D-K  ","FDCSJ225HKX2A-KT ","FDCSJ225HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ784HKX2DAF  ",null,"FDCSJ280HKX2D-K  ","FDCSJ225HKX2A-KT ","FDCSJ281HKX2A-KT ",null,{"$f":"12+5+7","v":24},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,24,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ840HKX2DAF  ",null,"FDCSJ280HKX2D-K  ","FDCSJ281HKX2A-KT ","FDCSJ281HKX2A-KT ",null,{"$f":"12+7+7","v":26},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,26,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ896HKX2DAF  ",null,"FDCSJ224HKX2D-K  ","FDCSJ225HKX2A-KT ","FDCSJ225HKX2A-KT ","FDCSJ225HKX2A-KT ",{"$f":"12+5+5+5","v":27},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,27,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ952HKX2DAF  ",null,"FDCSJ280HKX2D-K  ","FDCSJ225HKX2A-KT ","FDCSJ225HKX2A-KT ","FDCSJ225HKX2A-KT ",{"$f":"12+5+5+5","v":27},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,27,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ1008HKX2DAF  ",null,"FDCSJ280HKX2D-K  ","FDCSJ225HKX2A-KT ","FDCSJ225HKX2A-KT ","FDCSJ281HKX2A-KT ",{"$f":"12+5+5+7","v":29},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,29,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ1064HKX2DAF  ",null,"FDCSJ280HKX2D-K  ","FDCSJ225HKX2A-KT ","FDCSJ281HKX2A-KT ","FDCSJ281HKX2A-KT ",{"$f":"12+5+7+7","v":31},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,31,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R22","FDCSJ1120HKX2DAF  ",null,"FDCSJ280HKX2D-K  ","FDCSJ281HKX2A-KT ","FDCSJ281HKX2A-KT ","FDCSJ281HKX2A-KT ",{"$f":"12+7+7+7","v":33},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,33,{"$error":"#DIV/0!"},0.21,0.28000000000000003,0.5,{"$error":"#DIV/0!"}]
["R407C","FDCP224HKX2D    ","B",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP280HKX2D    ","B",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP355HKX2D    ","B",null,null,null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,16.350000000000001,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP450HKX2D    ","B",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,20,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP224HKX2D   ","B",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP280HKX2D   ","B",null,null,null,null,12,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP355HKX2D   ","B",null,null,null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,16.350000000000001,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP450HKX2D   ","B",null,null,null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",0,0,0,20,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP224HKX2D-K  ","B",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCP280HKX2D-K  ","B",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCSP224HKX2D-K ","B",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCSP280HKX2D-K ","B",null,null,null,null,12,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,12,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"},"組合せ専用機"]
["R407C","FDCP500HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP224HKX2A-KT ",null,null,{"$f":"12+5","v":17},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP560HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP280HKX2A-KT ",null,null,{"$f":"12+7","v":19},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,19,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP672HKX2DA  ",null,"FDCP224HKX2D-K  ","FDCP224HKX2A-KT ","FDCP224HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP728HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP224HKX2A-KT ","FDCP224HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP784HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP224HKX2A-KT ","FDCP280HKX2A-KT ",null,{"$f":"12+5+7","v":24},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,24,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP840HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP280HKX2A-KT ","FDCP280HKX2A-KT ",null,{"$f":"12+7+7","v":26},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,26,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP896HKX2DA  ",null,"FDCP224HKX2D-K  ","FDCP224HKX2A-KT ","FDCP224HKX2A-KT ","FDCP224HKX2A-KT ",{"$f":"12+5+5+5","v":27},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,27,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP952HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP224HKX2A-KT ","FDCP224HKX2A-KT ","FDCP224HKX2A-KT ",{"$f":"12+5+5+5","v":27},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,27,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP1008HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP224HKX2A-KT ","FDCP224HKX2A-KT ","FDCP280HKX2A-KT ",{"$f":"12+5+5+7","v":29},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,29,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP1064HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP224HKX2A-KT ","FDCP280HKX2A-KT ","FDCP280HKX2A-KT ",{"$f":"12+5+7+7","v":31},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,31,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP1120HKX2DA  ",null,"FDCP280HKX2D-K  ","FDCP280HKX2A-KT ","FDCP280HKX2A-KT ","FDCP280HKX2A-KT ",{"$f":"12+7+7+7","v":33},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,33,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP500HKX2DAF ",null,"FDCP280HKX2D-K  ","FDCP225HKX2A-KT ",null,null,{"$f":"12+5","v":17},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP560HKX2DAF  ",null,"FDCP280HKX2D-K  ","FDCP281HKX2A-KT ",null,null,{"$f":"12+7","v":19},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,19,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP672HKX2DAF  ",null,"FDCP224HKX2D-K  ","FDCP225HKX2A-KT ","FDCP225HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP728HKX2DAF  ",null,"FDCP280HKX2D-K  ","FDCP225HKX2A-KT ","FDCP225HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP784HKX2DAF  ",null,"FDCP280HKX2D-K  ","FDCP225HKX2A-KT ","FDCP281HKX2A-KT ",null,{"$f":"12+5+7","v":24},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,24,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP840HKX2DAF  ",null,"FDCP280HKX2D-K  ","FDCP281HKX2A-KT ","FDCP281HKX2A-KT ",null,{"$f":"12+7+7","v":26},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,26,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP896HKX2DAF  ",null,"FDCP224HKX2D-K  ","FDCP225HKX2A-KT ","FDCP225HKX2A-KT ","FDCP225HKX2A-KT ",{"$f":"12+5+5+5","v":27},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,{"$f":"V325","v":0},{"$f":"IF(S325+W325<0,0,S325+W325)","v":0},27,{"$error":"#DIV/0!"},{"$f":"IF(A325=\"R410A\",0.39,IF(A325=\"R407C\",0.27,IF(A325=\"R22\",0.21,\"NG\")))","v":0.27},{"$f":"IF(A325=\"R410A\",0.42,IF(A325=\"R407C\",0.46,IF(A325=\"R22\",0.28,\"NG\")))","v":0.46},{"$f":"IF(A325=\"R410A\",0.42,IF(A325=\"R407C\",0.49,IF(A325=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(OR(Z325<=AA325,AND(U325=\"その他\",Z325<=AB325)),\"OK\",IF(OR(AND(U325=\"最下層\",Z325<=AB325),AND(U325=\"その他\",Z325<=AC325)),\"対策が１つ必要です\",IF(OR(AND(U325=\"最下層\",Z325<=AC325),AND(U325=\"その他\",Z325>AC325)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R407C","FDCP952HKX2DAF  ",null,"FDCP280HKX2D-K  ","FDCP225HKX2A-KT ","FDCP225HKX2A-KT ","FDCP225HKX2A-KT ",{"$f":"12+5+5+5","v":27},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,{"$f":"H326+X326","v":27},{"$f":"Y326/I326","v":{"$error":"#DIV/0!"}},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP1008HKX2DAF  ",null,"FDCP280HKX2D-K  ","FDCP225HKX2A-KT ","FDCP225HKX2A-KT ","FDCP281HKX2A-KT ",{"$f":"12+5+5+7","v":29},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,29,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP1064HKX2DAF  ",null,"FDCP280HKX2D-K  ","FDCP225HKX2A-KT ","FDCP281HKX2A-KT ","FDCP281HKX2A-KT ",{"$f":"12+5+7+7","v":31},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,31,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP1120HKX2DAF  ",null,"FDCP280HKX2D-K  ","FDCP281HKX2A-KT ","FDCP281HKX2A-KT ","FDCP281HKX2A-KT ",{"$f":"12+7+7+7","v":33},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,33,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP500HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP224HKX2A-KT ",null,null,{"$f":"12+5","v":17},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP560HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP280HKX2A-KT ",null,null,{"$f":"12+7","v":19},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,19,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP672HKX2DA  ",null,"FDCSP224HKX2D-K  ","FDCSP224HKX2A-KT ","FDCSP224HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP728HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP224HKX2A-KT ","FDCSP224HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP784HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP224HKX2A-KT ","FDCSP280HKX2A-KT ",null,{"$f":"12+5+7","v":24},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,24,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP840HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP280HKX2A-KT ","FDCSP280HKX2A-KT ",null,{"$f":"12+7+7","v":26},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,26,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP896HKX2DA  ",null,"FDCSP224HKX2D-K  ","FDCSP224HKX2A-KT ","FDCSP224HKX2A-KT ","FDCSP224HKX2A-KT ",{"$f":"12+5+5+5","v":27},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,27,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP952HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP224HKX2A-KT ","FDCSP224HKX2A-KT ","FDCSP224HKX2A-KT ",{"$f":"12+5+5+5","v":27},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,27,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP1008HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP224HKX2A-KT ","FDCSP224HKX2A-KT ","FDCSP280HKX2A-KT ",{"$f":"12+5+5+7","v":29},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,{"$f":"IF(J338=\"φ6.4\",K338*L338,IF(J338=\"φ9.5\",K338*M338,IF(J338=\"φ12.7\",K338*N338,IF(J338=\"φ15.9\",K338*O338,IF(J338=\"φ19.1\",K338*P338,IF(J338=\"φ22.2\",K338*Q338,IF(J338=\"φ25.4\",K338*R338,0)))))))","v":0},null,"その他",0,0,0,29,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP1064HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP224HKX2A-KT ","FDCSP280HKX2A-KT ","FDCSP280HKX2A-KT ",{"$f":"12+5+7+7","v":31},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,31,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP1120HKX2DA  ",null,"FDCSP280HKX2D-K  ","FDCSP280HKX2A-KT ","FDCSP280HKX2A-KT ","FDCSP280HKX2A-KT ",{"$f":"12+7+7+7","v":33},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,33,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP500HKX2DAF ",null,"FDCSP280HKX2D-K  ","FDCSP225HKX2A-KT ",null,null,{"$f":"12+5","v":17},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP560HKX2DAF  ",null,"FDCSP280HKX2D-K  ","FDCSP281HKX2A-KT ",null,null,{"$f":"12+7","v":19},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,19,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP672HKX2DAF  ",null,"FDCSP224HKX2D-K  ","FDCSP225HKX2A-KT ","FDCSP225HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP728HKX2DAF  ",null,"FDCSP280HKX2D-K  ","FDCSP225HKX2A-KT ","FDCSP225HKX2A-KT ",null,{"$f":"12+5+5","v":22},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,22,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP784HKX2DAF  ",null,"FDCSP280HKX2D-K  ","FDCSP225HKX2A-KT ","FDCSP281HKX2A-KT ",null,{"$f":"12+5+7","v":24},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,24,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP840HKX2DAF  ",null,"FDCSP280HKX2D-K  ","FDCSP281HKX2A-KT ","FDCSP281HKX2A-KT ",null,{"$f":"12+7+7","v":26},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,26,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP896HKX2DAF  ",null,"FDCSP224HKX2D-K  ","FDCSP225HKX2A-KT ","FDCSP225HKX2A-KT ","FDCSP225HKX2A-KT ",{"$f":"12+5+5+5","v":27},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,27,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP952HKX2DAF  ",null,"FDCSP280HKX2D-K  ","FDCSP225HKX2A-KT ","FDCSP225HKX2A-KT ","FDCSP225HKX2A-KT ",{"$f":"12+5+5+5","v":27},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,27,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP1008HKX2DAF  ",null,"FDCSP280HKX2D-K  ","FDCSP225HKX2A-KT ","FDCSP225HKX2A-KT ","FDCSP281HKX2A-KT ",{"$f":"12+5+5+7","v":29},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,29,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP1064HKX2DAF  ",null,"FDCSP280HKX2D-K  ","FDCSP225HKX2A-KT ","FDCSP281HKX2A-KT ","FDCSP281HKX2A-KT ",{"$f":"12+5+7+7","v":31},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,31,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP1120HKX2DAF  ",null,"FDCSP280HKX2D-K  ","FDCSP281HKX2A-KT ","FDCSP281HKX2A-KT ","FDCSP281HKX2A-KT ",{"$f":"12+7+7+7","v":33},null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,0.4,0.53,0,null,"その他",0,0,0,33,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP280HKXIC1   ","B","ISUP355HC1","FDCP280HKXIC1   ",null,null,20,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",19,19,19,39,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP355HKXIC1   ","B","ISUP450HC1","FDCP355HKXIC1   ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",22,22,22,42,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP280HKXIC1  ","B","ISUSP355HC1","FDCSP280HKXIC1  ",null,null,20,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",19,19,19,39,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP355HKXIC1  ","B","ISUSP450HC1","FDCSP355HKXIC1  ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",22,22,22,42,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP280HKXIC1  ","C","ISUSP355HC1","FDCSP280HKXIC1  ",null,null,20,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",19,19,19,39,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP355HKXIC1  ","C","ISUSP450HC1","FDCSP355HKXIC1  ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,"***","***","***",0,null,"その他",22,22,22,42,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP280HKXIS1A  ","B","ISUP355HS1","FDCP280HKXIS1A  ",null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",17,17,17,33.35,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP355HKXIS1A  ","B","ISUP450HS1","FDCP355HKXIS1A  ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",26,26,26,46,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP450HKXIS1A  ","B","ISUP560HS1","FDCP450HKXIS1A  ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",26,26,26,46,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP280HKXIS1A ","B","ISUSP355HS1","FDCSP280HKXIS1A ",null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",17,17,17,33.35,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP355HKXIS1A ","B","ISUSP450HS1","FDCSP355HKXIS1A ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",26,26,26,46,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP450HKXIS1A ","B","ISUSP560HS1","FDCSP450HKXIS1A ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",26,26,26,46,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP280HKXIS1A ","C","ISUSP355HS1","FDCSP280HKXIS1A ",null,null,16.350000000000001,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",17,17,17,33.35,{"$error":"#DIV/0!"},0.27,0.46,{"$f":"IF(A364=\"R410A\",0.42,IF(A364=\"R407C\",0.49,IF(A364=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(OR(Z364<=AA364,AND(U364=\"その他\",Z364<=AB364)),\"OK\",IF(OR(AND(U364=\"最下層\",Z364<=AB364),AND(U364=\"その他\",Z364<=AC364)),\"対策が１つ必要です\",IF(OR(AND(U364=\"最下層\",Z364<=AC364),AND(U364=\"その他\",Z364>AC364)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R407C","FDCSP355HKXIS1A ","C","ISUSP450HS1","FDCSP355HKXIS1A ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",26,26,26,46,{"$error":"#DIV/0!"},0.27,0.46,{"$f":"IF(A365=\"R410A\",0.42,IF(A365=\"R407C\",0.49,IF(A365=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(OR(Z365<=AA365,AND(U365=\"その他\",Z365<=AB365)),\"OK\",IF(OR(AND(U365=\"最下層\",Z365<=AB365),AND(U365=\"その他\",Z365<=AC365)),\"対策が１つ必要です\",IF(OR(AND(U365=\"最下層\",Z365<=AC365),AND(U365=\"その他\",Z365>AC365)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R407C","FDCSP450HKXIS1A ","C","ISUSP560HS1","FDCSP450HKXIS1A ",null,null,20,null,null,null,0.03,0.06,0.12,0.2,0.28000000000000003,"***","***",0,null,"その他",26,26,26,46,{"$error":"#DIV/0!"},0.27,0.46,{"$f":"IF(A366=\"R410A\",0.42,IF(A366=\"R407C\",0.49,IF(A366=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(OR(Z366<=AA366,AND(U366=\"その他\",Z366<=AB366)),\"OK\",IF(OR(AND(U366=\"最下層\",Z366<=AB366),AND(U366=\"その他\",Z366<=AC366)),\"対策が１つ必要です\",IF(OR(AND(U366=\"最下層\",Z366<=AC366),AND(U366=\"その他\",Z366>AC366)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R407C","FDCP140HKX2DA   "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCSP140HKX2DA  "," ",null,null,null,null,9,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,9,{"$error":"#DIV/0!"},0.27,0.46,{"$f":"IF(A368=\"R410A\",0.42,IF(A368=\"R407C\",0.49,IF(A368=\"R22\",0.5,\"NG\")))","v":0.49},{"$f":"IF(OR(Z368<=AA368,AND(U368=\"その他\",Z368<=AB368)),\"OK\",IF(OR(AND(U368=\"最下層\",Z368<=AB368),AND(U368=\"その他\",Z368<=AC368)),\"対策が１つ必要です\",IF(OR(AND(U368=\"最下層\",Z368<=AC368),AND(U368=\"その他\",Z368>AC368)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R407C","FDCP224HKX3     "," ",null,null,null,null,14,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,14,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R407C","FDCP280HKX3     "," ",null,null,null,null,14,null,null,null,0.03,0.06,0.12,"***","***","***","***",0,null,"その他",0,0,0,14,{"$error":"#DIV/0!"},0.27,0.46,0.49,{"$error":"#DIV/0!"}]
["R410A","FDCP1401HLX     "," ",null,null,null,null,8.5,null,null,null,"***","***","***","***","***","***","***",0,null,"その他",0,0,0,8.5,{"$error":"#DIV/0!"},0.39,0.42,{"$f":"IF(A371=\"R410A\",0.42,IF(A371=\"R407C\",0.49,IF(A371=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z371<=AA371,AND(U371=\"その他\",Z371<=AB371)),\"OK\",IF(OR(AND(U371=\"最下層\",Z371<=AB371),AND(U371=\"その他\",Z371<=AC371)),\"対策が１つ必要です\",IF(OR(AND(U371=\"最下層\",Z371<=AC371),AND(U371=\"その他\",Z371>AC371)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCP1601HLX     "," ",null,null,null,null,8.5,null,null,null,"***","***","***","***","***","***","***",0,null,"その他",0,0,0,8.5,{"$error":"#DIV/0!"},0.39,0.42,{"$f":"IF(A372=\"R410A\",0.42,IF(A372=\"R407C\",0.49,IF(A372=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z372<=AA372,AND(U372=\"その他\",Z372<=AB372)),\"OK\",IF(OR(AND(U372=\"最下層\",Z372<=AB372),AND(U372=\"その他\",Z372<=AC372)),\"対策が１つ必要です\",IF(OR(AND(U372=\"最下層\",Z372<=AC372),AND(U372=\"その他\",Z372>AC372)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCP2241HLX     "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2801HLX     "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3351HLX     "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3351HLX-K   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4001HLX     "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4501HLX     "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5041HLX     "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5601HLX     "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6151HLX     "," ",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6801HLX     "," ",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP7351HLX",null,"FDCP3351HLX-K   ","FDCP4001HLX     ",null,null,{"$f":"H376+H377","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP8001HLX",null,"FDCP4001HLX     ","FDCP4001HLX     ",null,null,{"$f":"H377+H377","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP8501HLX",null,"FDCP4001HLX     ","FDCP4501HLX     ",null,null,{"$f":"H377+H378","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP9001HLX",null,"FDCP4501HLX     ","FDCP4501HLX     ",null,null,{"$f":"H378+H378","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP9601HLX",null,"FDCP4501HLX     ","FDCP5041HLX     ",null,null,{"$f":"H378+H379","v":36.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,36.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP10101HLX",null,"FDCP5041HLX     ","FDCP5041HLX     ",null,null,{"$f":"H379+H379","v":38.799999999999997},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,38.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP10651HLX",null,"FDCP5041HLX     ","FDCP5601HLX     ",null,null,{"$f":"H379+H380","v":38.799999999999997},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,{"$f":"V389","v":0},{"$f":"IF(S389+W389<0,0,S389+W389)","v":0},38.799999999999997,{"$error":"#DIV/0!"},{"$f":"IF(A389=\"R410A\",0.39,IF(A389=\"R407C\",0.27,IF(A389=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(A389=\"R410A\",0.42,IF(A389=\"R407C\",0.46,IF(A389=\"R22\",0.28,\"NG\")))","v":0.42},{"$f":"IF(A389=\"R410A\",0.42,IF(A389=\"R407C\",0.49,IF(A389=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z389<=AA389,AND(U389=\"その他\",Z389<=AB389)),\"OK\",IF(OR(AND(U389=\"最下層\",Z389<=AB389),AND(U389=\"その他\",Z389<=AC389)),\"対策が１つ必要です\",IF(OR(AND(U389=\"最下層\",Z389<=AC389),AND(U389=\"その他\",Z389>AC389)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCP11301HLX",null,"FDCP5601HLX     ","FDCP5601HLX     ",null,null,{"$f":"H380+H380","v":38.799999999999997},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,{"$f":"H390+X390","v":38.799999999999997},{"$f":"Y390/I390","v":{"$error":"#DIV/0!"}},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP11801HLX",null,"FDCP5601HLX     ","FDCP6151HLX     ",null,null,{"$f":"H380+H381","v":45.599999999999994},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,45.599999999999994,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP12351HLX",null,"FDCP6151HLX     ","FDCP6151HLX     ",null,null,{"$f":"H381+H381","v":52.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,52.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP13001HLX",null,"FDCP6151HLX     ","FDCP6801HLX     ",null,null,{"$f":"H381+H382","v":52.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,52.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP13601HLX",null,"FDCP6801HLX     ","FDCP6801HLX     ",null,null,{"$f":"H382+H382","v":52.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,52.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP1401HLX    "," ",null,null,null,null,8.5,null,null,null,"***","***","***","***","***","***","***",0,null,"その他",0,{"$f":"V395","v":0},{"$f":"IF(S395+W395<0,0,S395+W395)","v":0},8.5,{"$error":"#DIV/0!"},{"$f":"IF(A395=\"R410A\",0.39,IF(A395=\"R407C\",0.27,IF(A395=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(A395=\"R410A\",0.42,IF(A395=\"R407C\",0.46,IF(A395=\"R22\",0.28,\"NG\")))","v":0.42},{"$f":"IF(A395=\"R410A\",0.42,IF(A395=\"R407C\",0.49,IF(A395=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z395<=AA395,AND(U395=\"その他\",Z395<=AB395)),\"OK\",IF(OR(AND(U395=\"最下層\",Z395<=AB395),AND(U395=\"その他\",Z395<=AC395)),\"対策が１つ必要です\",IF(OR(AND(U395=\"最下層\",Z395<=AC395),AND(U395=\"その他\",Z395>AC395)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCSP1601HLX    "," ",null,null,null,null,8.5,null,null,null,"***","***","***","***","***","***","***",0,null,"その他",0,{"$f":"V396","v":0},{"$f":"IF(S396+W396<0,0,S396+W396)","v":0},8.5,{"$error":"#DIV/0!"},0.39,0.42,{"$f":"IF(A396=\"R410A\",0.42,IF(A396=\"R407C\",0.49,IF(A396=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z396<=AA396,AND(U396=\"その他\",Z396<=AB396)),\"OK\",IF(OR(AND(U396=\"最下層\",Z396<=AB396),AND(U396=\"その他\",Z396<=AC396)),\"対策が１つ必要です\",IF(OR(AND(U396=\"最下層\",Z396<=AC396),AND(U396=\"その他\",Z396>AC396)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCSP2241HLX    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,{"$f":"IF(S397+W397<0,0,S397+W397)","v":0},14.2,{"$error":"#DIV/0!"},0.39,0.42,{"$f":"IF(A397=\"R410A\",0.42,IF(A397=\"R407C\",0.49,IF(A397=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z397<=AA397,AND(U397=\"その他\",Z397<=AB397)),\"OK\",IF(OR(AND(U397=\"最下層\",Z397<=AB397),AND(U397=\"その他\",Z397<=AC397)),\"対策が１つ必要です\",IF(OR(AND(U397=\"最下層\",Z397<=AC397),AND(U397=\"その他\",Z397>AC397)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCSP2801HLX    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3351HLX    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3351HLX-K  "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4001HLX    "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4501HLX    "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J402=\"φ6.4\",K402*L402,IF(J402=\"φ9.5\",K402*M402,IF(J402=\"φ12.7\",K402*N402,IF(J402=\"φ15.9\",K402*O402,IF(J402=\"φ19.1\",K402*P402,IF(J402=\"φ22.2\",K402*Q402,IF(J402=\"φ25.4\",K402*R402,0)))))))","v":0},null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5041HLX    "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5601HLX    "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6151HLX    "," ",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6801HLX    "," ",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP2241HLX    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP2801HLX    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP2801HLX-K  "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP3351HLX    "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP4001HLX    "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP4501HLX    "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP5041HLX    "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP5601HLX    "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,{"$f":"V414","v":0},{"$f":"IF(S414+W414<0,0,S414+W414)","v":0},19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP6151HLX     ",null,"FDCRP2801HLX-K  ","FDCRP3351HLX    ",null,null,{"$f":"H409+H410","v":31.2},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,{"$f":"V415","v":0},{"$f":"IF(S415+W415<0,0,S415+W415)","v":0},31.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP6801HLX     ",null,"FDCRP3351HLX    ","FDCRP3351HLX    ",null,null,{"$f":"H410+H410","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP7351HLX",null,"FDCRP3351HLX    ","FDCRP4001HLX    ",null,null,{"$f":"H410+H411","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP8001HLX",null,"FDCRP4001HLX    ","FDCRP4001HLX    ",null,null,{"$f":"H411+H411","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP8501HLX",null,"FDCRP4001HLX    ","FDCRP4501HLX    ",null,null,{"$f":"H411+H412","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP9001HLX",null,"FDCRP4501HLX    ","FDCRP4501HLX    ",null,null,{"$f":"H412+H412","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP9601HLX",null,"FDCRP4501HLX    ","FDCRP5041HLX    ",null,null,{"$f":"H412+H413","v":36.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,36.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP10101HLX",null,"FDCRP5041HLX    ","FDCRP5041HLX    ",null,null,{"$f":"H413+H413","v":38.799999999999997},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,38.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP2241HLX   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,{"$f":"V423","v":0},{"$f":"IF(S423+W423<0,0,S423+W423)","v":0},14.2,{"$error":"#DIV/0!"},0.39,0.42,{"$f":"IF(A423=\"R410A\",0.42,IF(A423=\"R407C\",0.49,IF(A423=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z423<=AA423,AND(U423=\"その他\",Z423<=AB423)),\"OK\",IF(OR(AND(U423=\"最下層\",Z423<=AB423),AND(U423=\"その他\",Z423<=AC423)),\"対策が１つ必要です\",IF(OR(AND(U423=\"最下層\",Z423<=AC423),AND(U423=\"その他\",Z423>AC423)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCRSP2801HLX   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP2801HLX-K "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP3351HLX   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP4001HLX   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},{"$f":"IF(A427=\"R410A\",0.39,IF(A427=\"R407C\",0.27,IF(A427=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(A427=\"R410A\",0.42,IF(A427=\"R407C\",0.46,IF(A427=\"R22\",0.28,\"NG\")))","v":0.42},0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP4501HLX   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP5041HLX   "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP5601HLX   "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J430=\"φ6.4\",K430*L430,IF(J430=\"φ9.5\",K430*M430,IF(J430=\"φ12.7\",K430*N430,IF(J430=\"φ15.9\",K430*O430,IF(J430=\"φ19.1\",K430*P430,IF(J430=\"φ22.2\",K430*Q430,IF(J430=\"φ25.4\",K430*R430,0)))))))","v":0},null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2241HLXR    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J431=\"φ6.4\",K431*L431,IF(J431=\"φ9.5\",K431*M431,IF(J431=\"φ12.7\",K431*N431,IF(J431=\"φ15.9\",K431*O431,IF(J431=\"φ19.1\",K431*P431,IF(J431=\"φ22.2\",K431*Q431,IF(J431=\"φ25.4\",K431*R431,0)))))))*1.3","v":0},null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2801HLXR    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J432=\"φ6.4\",K432*L432,IF(J432=\"φ9.5\",K432*M432,IF(J432=\"φ12.7\",K432*N432,IF(J432=\"φ15.9\",K432*O432,IF(J432=\"φ19.1\",K432*P432,IF(J432=\"φ22.2\",K432*Q432,IF(J432=\"φ25.4\",K432*R432,0)))))))*1.3","v":0},null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3351HLXR    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3351HLXR-K  "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4001HLXR    "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4501HLXR    "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5041HLXR    "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5601HLXR    "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6151HLXR    "," ",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6801HLXR    "," ",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP7351HLXR",null,"FDCP3351HLXR-K  ","FDCP4001HLXR    ",null,null,{"$f":"H434+H435","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J441=\"φ6.4\",K441*L441,IF(J441=\"φ9.5\",K441*M441,IF(J441=\"φ12.7\",K441*N441,IF(J441=\"φ15.9\",K441*O441,IF(J441=\"φ19.1\",K441*P441,IF(J441=\"φ22.2\",K441*Q441,IF(J441=\"φ25.4\",K441*R441,0)))))))*1.2","v":0},null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP8001HLXR",null,"FDCP4001HLXR    ","FDCP4001HLXR    ",null,null,{"$f":"H435+H435","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J442=\"φ6.4\",K442*L442,IF(J442=\"φ9.5\",K442*M442,IF(J442=\"φ12.7\",K442*N442,IF(J442=\"φ15.9\",K442*O442,IF(J442=\"φ19.1\",K442*P442,IF(J442=\"φ22.2\",K442*Q442,IF(J442=\"φ25.4\",K442*R442,0)))))))*1.2","v":0},null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP8501HLXR",null,"FDCP4001HLXR    ","FDCP4501HLXR    ",null,null,{"$f":"H435+H436","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP9001HLXR",null,"FDCP4501HLXR    ","FDCP4501HLXR    ",null,null,{"$f":"H436+H436","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP9601HLXR",null,"FDCP4501HLXR    ","FDCP5041HLXR    ",null,null,{"$f":"H436+H437","v":36.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,36.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP10101HLXR",null,"FDCP5041HLXR    ","FDCP5041HLXR    ",null,null,{"$f":"H437+H437","v":38.799999999999997},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,38.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP10651HLXR",null,"FDCP5041HLXR    ","FDCP5601HLXR    ",null,null,{"$f":"H437+H438","v":38.799999999999997},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,38.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP11301HLXR",null,"FDCP5601HLXR    ","FDCP5601HLXR    ",null,null,{"$f":"H438+H438","v":38.799999999999997},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,38.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP11801HLXR",null,"FDCP5601HLXR    ","FDCP6151HLXR    ",null,null,{"$f":"H438+H439","v":45.599999999999994},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,45.599999999999994,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP12351HLXR",null,"FDCP6151HLXR    ","FDCP6151HLXR    ",null,null,{"$f":"H439+H439","v":52.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,52.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP13001HLXR",null,"FDCP6151HLXR    ","FDCP6801HLXR    ",null,null,{"$f":"H439+H440","v":52.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,52.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP13601HLXR",null,"FDCP6801HLXR    ","FDCP6801HLXR    ",null,null,{"$f":"H440+H440","v":52.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,52.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2241HLXR   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J453=\"φ6.4\",K453*L453,IF(J453=\"φ9.5\",K453*M453,IF(J453=\"φ12.7\",K453*N453,IF(J453=\"φ15.9\",K453*O453,IF(J453=\"φ19.1\",K453*P453,IF(J453=\"φ22.2\",K453*Q453,IF(J453=\"φ25.4\",K453*R453,0)))))))*1.3","v":0},null,"その他",0,{"$f":"V453","v":0},{"$f":"IF(S453+W453<0,0,S453+W453)","v":0},14.2,{"$error":"#DIV/0!"},0.39,0.42,{"$f":"IF(A453=\"R410A\",0.42,IF(A453=\"R407C\",0.49,IF(A453=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z453<=AA453,AND(U453=\"その他\",Z453<=AB453)),\"OK\",IF(OR(AND(U453=\"最下層\",Z453<=AB453),AND(U453=\"その他\",Z453<=AC453)),\"対策が１つ必要です\",IF(OR(AND(U453=\"最下層\",Z453<=AC453),AND(U453=\"その他\",Z453>AC453)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCSP2801HLXR   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J454=\"φ6.4\",K454*L454,IF(J454=\"φ9.5\",K454*M454,IF(J454=\"φ12.7\",K454*N454,IF(J454=\"φ15.9\",K454*O454,IF(J454=\"φ19.1\",K454*P454,IF(J454=\"φ22.2\",K454*Q454,IF(J454=\"φ25.4\",K454*R454,0)))))))*1.3","v":0},null,"その他",0,0,0,{"$f":"H454+X454","v":14.2},{"$f":"Y454/I454","v":{"$error":"#DIV/0!"}},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3351HLXR   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3351HLXR-K "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4001HLXR   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4501HLXR   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5041HLXR   "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},{"$f":"IF(A459=\"R410A\",0.39,IF(A459=\"R407C\",0.27,IF(A459=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(A459=\"R410A\",0.42,IF(A459=\"R407C\",0.46,IF(A459=\"R22\",0.28,\"NG\")))","v":0.42},0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5601HLXR   "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6151HLXR   "," ",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6801HLXR   "," ",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2241HLX     ","A",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J463=\"φ6.4\",K463*L463,IF(J463=\"φ9.5\",K463*M463,IF(J463=\"φ12.7\",K463*N463,IF(J463=\"φ15.9\",K463*O463,IF(J463=\"φ19.1\",K463*P463,IF(J463=\"φ22.2\",K463*Q463,IF(J463=\"φ25.4\",K463*R463,0)))))))","v":0},null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2801HLX     ","A",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J464=\"φ6.4\",K464*L464,IF(J464=\"φ9.5\",K464*M464,IF(J464=\"φ12.7\",K464*N464,IF(J464=\"φ15.9\",K464*O464,IF(J464=\"φ19.1\",K464*P464,IF(J464=\"φ22.2\",K464*Q464,IF(J464=\"φ25.4\",K464*R464,0)))))))","v":0},null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3351HLX     ","A",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4501HLX     ","A",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5041HLX     ","A",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5601HLX     ","A",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6151HLX     ","A",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6801HLX     ","A",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2241HLX    ","A",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2801HLX    ","A",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3351HLX    ","A",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4501HLX    ","A",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5041HLX    ","A",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5601HLX    ","A",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6151HLX    ","A",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6801HLX    ","A",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2801HLXI    "," ","ISUP5601HLX","FDCP2801HLXI    ",null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",3,{"$f":"V479","v":3},{"$f":"IF(S479+W479<0,0,S479+W479)","v":3},17.2,{"$error":"#DIV/0!"},{"$f":"IF(A479=\"R410A\",0.39,IF(A479=\"R407C\",0.27,IF(A479=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(A479=\"R410A\",0.42,IF(A479=\"R407C\",0.46,IF(A479=\"R22\",0.28,\"NG\")))","v":0.42},{"$f":"IF(A479=\"R410A\",0.42,IF(A479=\"R407C\",0.49,IF(A479=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z479<=AA479,AND(U479=\"その他\",Z479<=AB479)),\"OK\",IF(OR(AND(U479=\"最下層\",Z479<=AB479),AND(U479=\"その他\",Z479<=AC479)),\"対策が１つ必要です\",IF(OR(AND(U479=\"最下層\",Z479<=AC479),AND(U479=\"その他\",Z479>AC479)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCP3351HLXI    "," ","ISUP5601HLX","FDCP3351HLXI    ",null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",2,2,2,16.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4501HLXI    "," ","ISUP5601HLX","FDCP4501HLXI    ",null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",2,2,2,19,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2801HLXI   "," ","ISUSP5601HLX","FDCSP2801HLXI   ",null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",3,3,3,17.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3351HLXI   "," ","ISUSP5601HLX","FDCSP3351HLXI   ",null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",2,2,2,16.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4501HLXI   "," ","ISUSP5601HLX","FDCSP4501HLXI   ",null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",2,2,2,19,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP1402HLX     "," ",null,null,null,null,7.5,null,null,null,"***","***","***","***","***","***","***",0,null,"その他",0,0,0,7.5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP1602HLX     "," ",null,null,null,null,7.5,null,null,null,"***","***","***","***","***","***","***",0,null,"その他",0,0,0,7.5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2242HLX     "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2802HLX     "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3352HLX     "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3352HLX-K   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4002HLX     "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4502HLX     "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5042HLX     "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5602HLX     "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6152HLX     "," ",null,null,null,null,21.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,21.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6802HLX     "," ",null,null,null,null,21.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,21.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP7352HLX",null,"FDCP3352HLX-K   ","FDCP4002HLX     ",null,null,{"$f":"H490+H491","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP8002HLX",null,"FDCP4002HLX     ","FDCP4002HLX     ",null,null,{"$f":"H491+H491","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP8502HLX",null,"FDCP4002HLX     ","FDCP4502HLX     ",null,null,{"$f":"H491+H492","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP9002HLX",null,"FDCP4502HLX     ","FDCP4502HLX     ",null,null,{"$f":"H492+H492","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP9602HLX",null,"FDCP4502HLX     ","FDCP5042HLX     ",null,null,{"$f":"H492+H493","v":36.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,36.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP10102HLX",null,"FDCP5042HLX     ","FDCP5042HLX     ",null,null,{"$f":"H493+H493","v":38.799999999999997},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,38.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP10652HLX",null,"FDCP5042HLX     ","FDCP5602HLX     ",null,null,{"$f":"H493+H494","v":38.799999999999997},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,38.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP11302HLX",null,"FDCP5602HLX     ","FDCP5602HLX     ",null,null,{"$f":"H494+H494","v":38.799999999999997},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,38.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP11802HLX",null,"FDCP5602HLX     ","FDCP6152HLX     ",null,null,{"$f":"H494+H495","v":40.599999999999994},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,40.599999999999994,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP12352HLX",null,"FDCP6152HLX     ","FDCP6152HLX     ",null,null,{"$f":"H495+H495","v":42.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,42.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP13002HLX",null,"FDCP6152HLX     ","FDCP6802HLX     ",null,null,{"$f":"H495+H496","v":42.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,42.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP13602HLX",null,"FDCP6802HLX     ","FDCP6802HLX     ",null,null,{"$f":"H496+H496","v":42.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,42.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP1402HLX    "," ",null,null,null,null,7.5,null,null,null,"***","***","***","***","***","***","***",0,null,"その他",0,{"$f":"V509","v":0},{"$f":"IF(S509+W509<0,0,S509+W509)","v":0},7.5,{"$error":"#DIV/0!"},{"$f":"IF(A509=\"R410A\",0.39,IF(A509=\"R407C\",0.27,IF(A509=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(A509=\"R410A\",0.42,IF(A509=\"R407C\",0.46,IF(A509=\"R22\",0.28,\"NG\")))","v":0.42},{"$f":"IF(A509=\"R410A\",0.42,IF(A509=\"R407C\",0.49,IF(A509=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z509<=AA509,AND(U509=\"その他\",Z509<=AB509)),\"OK\",IF(OR(AND(U509=\"最下層\",Z509<=AB509),AND(U509=\"その他\",Z509<=AC509)),\"対策が１つ必要です\",IF(OR(AND(U509=\"最下層\",Z509<=AC509),AND(U509=\"その他\",Z509>AC509)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCSP1602HLX    "," ",null,null,null,null,7.5,null,null,null,"***","***","***","***","***","***","***",0,null,"その他",0,0,0,7.5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2242HLX    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2802HLX    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3352HLX    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3352HLX-K  "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4002HLX    "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4502HLX    "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5042HLX    "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5602HLX    "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,{"$f":"H518+X518","v":19.399999999999999},{"$f":"Y518/I518","v":{"$error":"#DIV/0!"}},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6152HLX    "," ",null,null,null,null,21.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,21.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6802HLX    "," ",null,null,null,null,21.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,21.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2242HLXR    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J521=\"φ6.4\",K521*L521,IF(J521=\"φ9.5\",K521*M521,IF(J521=\"φ12.7\",K521*N521,IF(J521=\"φ15.9\",K521*O521,IF(J521=\"φ19.1\",K521*P521,IF(J521=\"φ22.2\",K521*Q521,IF(J521=\"φ25.4\",K521*R521,0)))))))*1.3","v":0},null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2802HLXR    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J522=\"φ6.4\",K522*L522,IF(J522=\"φ9.5\",K522*M522,IF(J522=\"φ12.7\",K522*N522,IF(J522=\"φ15.9\",K522*O522,IF(J522=\"φ19.1\",K522*P522,IF(J522=\"φ22.2\",K522*Q522,IF(J522=\"φ25.4\",K522*R522,0)))))))*1.3","v":0},null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3352HLXR    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3352HLXR-K  "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4002HLXR    "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4502HLXR    "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5042HLXR    "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5602HLXR    "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6152HLXR    "," ",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6802HLXR    "," ",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP7352HLXR",null,"FDCP3352HLXR-K   ","FDCP4002HLXR     ",null,null,{"$f":"H524+H525","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J531=\"φ6.4\",K531*L531,IF(J531=\"φ9.5\",K531*M531,IF(J531=\"φ12.7\",K531*N531,IF(J531=\"φ15.9\",K531*O531,IF(J531=\"φ19.1\",K531*P531,IF(J531=\"φ22.2\",K531*Q531,IF(J531=\"φ25.4\",K531*R531,0)))))))*1.2","v":0},null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP8002HLXR",null,"FDCP4002HLXR   ","FDCP4002HLXR     ",null,null,{"$f":"H525+H525","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J532=\"φ6.4\",K532*L532,IF(J532=\"φ9.5\",K532*M532,IF(J532=\"φ12.7\",K532*N532,IF(J532=\"φ15.9\",K532*O532,IF(J532=\"φ19.1\",K532*P532,IF(J532=\"φ22.2\",K532*Q532,IF(J532=\"φ25.4\",K532*R532,0)))))))*1.2","v":0},null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP8502HLXR",null,"FDCP4002HLXR     ","FDCP4502HLXR     ",null,null,{"$f":"H525+H526","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP9002HLXR",null,"FDCP4502HLXR     ","FDCP4502HLXR     ",null,null,{"$f":"H526+H526","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP9602HLXR",null,"FDCP4502HLXR     ","FDCP5042HLXR     ",null,null,{"$f":"H526+H527","v":36.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,36.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP10102HLXR",null,"FDCP5042HLXR     ","FDCP5042HLXR     ",null,null,{"$f":"H527+H527","v":38.799999999999997},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,38.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP10652HLXR",null,"FDCP5042HLXR     ","FDCP5602HLXR     ",null,null,{"$f":"H527+H528","v":38.799999999999997},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,38.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP11302HLXR",null,"FDCP5602HLXR     ","FDCP5602HLXR     ",null,null,{"$f":"H528+H528","v":38.799999999999997},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,38.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP11802HLXR",null,"FDCP5602HLXR     ","FDCP6152HLXR     ",null,null,{"$f":"H528+H529","v":45.599999999999994},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,45.599999999999994,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP12352HLXR",null,"FDCP6152HLXR     ","FDCP6152HLXR     ",null,null,{"$f":"H529+H529","v":52.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,52.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP13002HLXR",null,"FDCP6152HLXR     ","FDCP6802HLXR     ",null,null,{"$f":"H529+H530","v":52.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,52.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP13602HLXR",null,"FDCP6802HLXR     ","FDCP6802HLXR     ",null,null,{"$f":"H530+H530","v":52.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,52.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2242HLXR   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J543=\"φ6.4\",K543*L543,IF(J543=\"φ9.5\",K543*M543,IF(J543=\"φ12.7\",K543*N543,IF(J543=\"φ15.9\",K543*O543,IF(J543=\"φ19.1\",K543*P543,IF(J543=\"φ22.2\",K543*Q543,IF(J543=\"φ25.4\",K543*R543,0)))))))*1.3","v":0},null,"その他",0,{"$f":"V543","v":0},{"$f":"IF(S543+W543<0,0,S543+W543)","v":0},14.2,{"$error":"#DIV/0!"},{"$f":"IF(A543=\"R410A\",0.39,IF(A543=\"R407C\",0.27,IF(A543=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(A543=\"R410A\",0.42,IF(A543=\"R407C\",0.46,IF(A543=\"R22\",0.28,\"NG\")))","v":0.42},{"$f":"IF(A543=\"R410A\",0.42,IF(A543=\"R407C\",0.49,IF(A543=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z543<=AA543,AND(U543=\"その他\",Z543<=AB543)),\"OK\",IF(OR(AND(U543=\"最下層\",Z543<=AB543),AND(U543=\"その他\",Z543<=AC543)),\"対策が１つ必要です\",IF(OR(AND(U543=\"最下層\",Z543<=AC543),AND(U543=\"その他\",Z543>AC543)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCSP2802HLXR   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J544=\"φ6.4\",K544*L544,IF(J544=\"φ9.5\",K544*M544,IF(J544=\"φ12.7\",K544*N544,IF(J544=\"φ15.9\",K544*O544,IF(J544=\"φ19.1\",K544*P544,IF(J544=\"φ22.2\",K544*Q544,IF(J544=\"φ25.4\",K544*R544,0)))))))*1.3","v":0},null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3352HLXR   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3352HLXR-K "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4002HLXR   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4502HLXR   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5042HLXR   "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5602HLXR   "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6152HLXR   "," ",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6802HLXR   "," ",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP2242HLX    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J553=\"φ6.4\",K553*L553,IF(J553=\"φ9.5\",K553*M553,IF(J553=\"φ12.7\",K553*N553,IF(J553=\"φ15.9\",K553*O553,IF(J553=\"φ19.1\",K553*P553,IF(J553=\"φ22.2\",K553*Q553,IF(J553=\"φ25.4\",K553*R553,0)))))))","v":0},null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP2802HLX    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J554=\"φ6.4\",K554*L554,IF(J554=\"φ9.5\",K554*M554,IF(J554=\"φ12.7\",K554*N554,IF(J554=\"φ15.9\",K554*O554,IF(J554=\"φ19.1\",K554*P554,IF(J554=\"φ22.2\",K554*Q554,IF(J554=\"φ25.4\",K554*R554,0)))))))","v":0},null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP2802HLX-K  "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP3352HLX    "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP4002HLX    "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP4502HLX    "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP5042HLX    "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP5602HLX    "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP6152HLX     ",null,"FDCRP2802HLX-K  ","FDCRP3352HLX    ",null,null,{"$f":"H555+H556","v":31.2},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,{"$f":"V561","v":0},{"$f":"IF(S561+W561<0,0,S561+W561)","v":0},31.2,{"$error":"#DIV/0!"},{"$f":"IF(A561=\"R410A\",0.39,IF(A561=\"R407C\",0.27,IF(A561=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(A561=\"R410A\",0.42,IF(A561=\"R407C\",0.46,IF(A561=\"R22\",0.28,\"NG\")))","v":0.42},{"$f":"IF(A561=\"R410A\",0.42,IF(A561=\"R407C\",0.49,IF(A561=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z561<=AA561,AND(U561=\"その他\",Z561<=AB561)),\"OK\",IF(OR(AND(U561=\"最下層\",Z561<=AB561),AND(U561=\"その他\",Z561<=AC561)),\"対策が１つ必要です\",IF(OR(AND(U561=\"最下層\",Z561<=AC561),AND(U561=\"その他\",Z561>AC561)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCRP6802HLX     ",null,"FDCRP3352HLX    ","FDCRP3352HLX    ",null,null,{"$f":"H556+H556","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP7352HLX",null,"FDCRP3352HLX    ","FDCRP4002HLX    ",null,null,{"$f":"H556+H557","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP8002HLX",null,"FDCRP4002HLX    ","FDCRP4002HLX    ",null,null,{"$f":"H557+H557","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP8502HLX",null,"FDCRP4002HLX    ","FDCRP4502HLX    ",null,null,{"$f":"H557+H558","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP9002HLX",null,"FDCRP4502HLX    ","FDCRP4502HLX    ",null,null,{"$f":"H558+H558","v":34},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP9602HLX",null,"FDCRP4502HLX    ","FDCRP5042HLX    ",null,null,{"$f":"H558+H559","v":36.4},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,36.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP10102HLX",null,"FDCRP5042HLX    ","FDCRP5042HLX    ",null,null,{"$f":"H559+H559","v":38.799999999999997},null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,38.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP2242HLX   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,{"$f":"V569","v":0},{"$f":"IF(S569+W569<0,0,S569+W569)","v":0},14.2,{"$error":"#DIV/0!"},{"$f":"IF(A569=\"R410A\",0.39,IF(A569=\"R407C\",0.27,IF(A569=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(A569=\"R410A\",0.42,IF(A569=\"R407C\",0.46,IF(A569=\"R22\",0.28,\"NG\")))","v":0.42},{"$f":"IF(A569=\"R410A\",0.42,IF(A569=\"R407C\",0.49,IF(A569=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z569<=AA569,AND(U569=\"その他\",Z569<=AB569)),\"OK\",IF(OR(AND(U569=\"最下層\",Z569<=AB569),AND(U569=\"その他\",Z569<=AC569)),\"対策が１つ必要です\",IF(OR(AND(U569=\"最下層\",Z569<=AC569),AND(U569=\"その他\",Z569>AC569)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCRSP2802HLX   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP2802HLX-K "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP3352HLX   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP4002HLX   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP4502HLX   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP5042HLX   "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP5602HLX   "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2802HLXI    "," ","ISUP5602HLX","FDCP2802HLXI    ",null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",3,3,3,17.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3352HLXI    "," ","ISUP5602HLX","FDCP3352HLXI    ",null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",2,2,2,16.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4502HLXI    "," ","ISUP5602HLX","FDCP4502HLXI    ",null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",2,2,2,19,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2802HLXI   "," ","ISUSP5602HLX","FDCSP2802HLXI   ",null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",3,3,3,17.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3352HLXI   "," ","ISUSP5602HLX","FDCSP3352HLXI   ",null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",2,2,2,16.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4502HLXI   "," ","ISUSP5602HLX","FDCSP4502HLXI   ",null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",2,2,2,{"$f":"H582+X582","v":19},{"$f":"Y582/I582","v":{"$error":"#DIV/0!"}},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP1402HLXB    "," ",null,null,null,null,7.5,null,null,null,"***","***","***","***","***","***","***",0,null,"その他",0,0,0,7.5,{"$error":"#DIV/0!"},0.39,0.42,{"$f":"IF(A583=\"R410A\",0.42,IF(A583=\"R407C\",0.49,IF(A583=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z583<=AA583,AND(U583=\"その他\",Z583<=AB583)),\"OK\",IF(OR(AND(U583=\"最下層\",Z583<=AB583),AND(U583=\"その他\",Z583<=AC583)),\"対策が１つ必要です\",IF(OR(AND(U583=\"最下層\",Z583<=AC583),AND(U583=\"その他\",Z583>AC583)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCP1602HLXB    "," ",null,null,null,null,7.5,null,null,null,"***","***","***","***","***","***","***",0,null,"その他",0,0,0,7.5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2242HLXB    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,{"$f":"V585","v":0},{"$f":"IF(S585+W585<0,0,S585+W585)","v":0},14.2,{"$error":"#DIV/0!"},{"$f":"IF(A585=\"R410A\",0.39,IF(A585=\"R407C\",0.27,IF(A585=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(A585=\"R410A\",0.42,IF(A585=\"R407C\",0.46,IF(A585=\"R22\",0.28,\"NG\")))","v":0.42},0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2802HLXB    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3352HLXB    "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3352HLXB-K  "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4002HLXB    "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4502HLXB    "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5042HLXB    "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5602HLXB    "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6152HLXB    "," ",null,null,null,null,21.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,21.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6802HLXB    "," ",null,null,null,null,21.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,21.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2802HLXIB   "," ","ISUP5602HLX","FDCP2802HLXIB   ",null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",3,3,3,17.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3352HLXIB   "," ","ISUP5602HLX","FDCP3352HLXIB   ",null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",2,2,2,16.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4502HLXIB   "," ","ISUP5602HLX","FDCP4502HLXIB   ",null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",2,2,2,19,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2242HLXRB   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J598=\"φ6.4\",K598*L598,IF(J598=\"φ9.5\",K598*M598,IF(J598=\"φ12.7\",K598*N598,IF(J598=\"φ15.9\",K598*O598,IF(J598=\"φ19.1\",K598*P598,IF(J598=\"φ22.2\",K598*Q598,IF(J598=\"φ25.4\",K598*R598,0)))))))*1.3","v":0},null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2802HLXRB   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J599=\"φ6.4\",K599*L599,IF(J599=\"φ9.5\",K599*M599,IF(J599=\"φ12.7\",K599*N599,IF(J599=\"φ15.9\",K599*O599,IF(J599=\"φ19.1\",K599*P599,IF(J599=\"φ22.2\",K599*Q599,IF(J599=\"φ25.4\",K599*R599,0)))))))*1.3","v":0},null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3352HLXRB   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3352HLXRB-K "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4002HLXRB   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4502HLXRB   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5042HLXRB   "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5602HLXRB   "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6152HLXRB   "," ",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6802HLXRB   "," ",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP2242HLXB   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J608=\"φ6.4\",K608*L608,IF(J608=\"φ9.5\",K608*M608,IF(J608=\"φ12.7\",K608*N608,IF(J608=\"φ15.9\",K608*O608,IF(J608=\"φ19.1\",K608*P608,IF(J608=\"φ22.2\",K608*Q608,IF(J608=\"φ25.4\",K608*R608,0)))))))","v":0},null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP2802HLXB   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J609=\"φ6.4\",K609*L609,IF(J609=\"φ9.5\",K609*M609,IF(J609=\"φ12.7\",K609*N609,IF(J609=\"φ15.9\",K609*O609,IF(J609=\"φ19.1\",K609*P609,IF(J609=\"φ22.2\",K609*Q609,IF(J609=\"φ25.4\",K609*R609,0)))))))","v":0},null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP2802HLXB-K "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP3352HLXB   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP4002HLXB   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP4502HLXB   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP5042HLXB   "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP5602HLXB   "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP2242HLXB  "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP2802HLXB  "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP2802HLXB-K"," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP3352HLXB  "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP4002HLXB  "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP4502HLXB  "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP5042HLXB  "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP5602HLXB  "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP1402HLXB   "," ",null,null,null,null,7.5,null,null,null,"***","***","***","***","***","***","***",0,null,"その他",0,0,0,7.5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP1602HLXB   "," ",null,null,null,null,7.5,null,null,null,"***","***","***","***","***","***","***",0,null,"その他",0,0,0,7.5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2242HLXB   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2802HLXB   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3352HLXB   "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3352HLXB-K "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4002HLXB   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4502HLXB   "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5042HLXB   "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5602HLXB   "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6152HLXB   "," ",null,null,null,null,21.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,21.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6802HLXB   "," ",null,null,null,null,21.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,21.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2802HLXIB  "," ","ISUSP5602HLX","FDCSP2802HLXIB  ",null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",3,3,3,17.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3352HLXIB  "," ","ISUSP5602HLX","FDCSP3352HLXIB  ",null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",2,2,2,16.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4502HLXIB  "," ","ISUSP5602HLX","FDCSP4502HLXIB  ",null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",2,2,2,19,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2242HLXRB  "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J639=\"φ6.4\",K639*L639,IF(J639=\"φ9.5\",K639*M639,IF(J639=\"φ12.7\",K639*N639,IF(J639=\"φ15.9\",K639*O639,IF(J639=\"φ19.1\",K639*P639,IF(J639=\"φ22.2\",K639*Q639,IF(J639=\"φ25.4\",K639*R639,0)))))))*1.3","v":0},null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2802HLXRB  "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J640=\"φ6.4\",K640*L640,IF(J640=\"φ9.5\",K640*M640,IF(J640=\"φ12.7\",K640*N640,IF(J640=\"φ15.9\",K640*O640,IF(J640=\"φ19.1\",K640*P640,IF(J640=\"φ22.2\",K640*Q640,IF(J640=\"φ25.4\",K640*R640,0)))))))*1.3","v":0},null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3352HLXRB  "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3352HLXRB-K"," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4002HLXRB  "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4502HLXRB  "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5042HLXRB  "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5602HLXRB  "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,{"$f":"H646+X646","v":19.399999999999999},{"$f":"Y646/I646","v":{"$error":"#DIV/0!"}},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6152HLXRB  "," ",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,{"$f":"IF(A647=\"R410A\",0.42,IF(A647=\"R407C\",0.49,IF(A647=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z647<=AA647,AND(U647=\"その他\",Z647<=AB647)),\"OK\",IF(OR(AND(U647=\"最下層\",Z647<=AB647),AND(U647=\"その他\",Z647<=AC647)),\"対策が１つ必要です\",IF(OR(AND(U647=\"最下層\",Z647<=AC647),AND(U647=\"その他\",Z647>AC647)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCSP6802HLXRB  "," ",null,null,null,null,26.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,26.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2242HLXB-V  "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J649=\"φ6.4\",K649*L649,IF(J649=\"φ9.5\",K649*M649,IF(J649=\"φ12.7\",K649*N649,IF(J649=\"φ15.9\",K649*O649,IF(J649=\"φ19.1\",K649*P649,IF(J649=\"φ22.2\",K649*Q649,IF(J649=\"φ25.4\",K649*R649,0)))))))","v":0},null,"その他",0,{"$f":"V649","v":0},{"$f":"IF(S649+W649<0,0,S649+W649)","v":0},14.2,{"$error":"#DIV/0!"},{"$f":"IF(A649=\"R410A\",0.39,IF(A649=\"R407C\",0.27,IF(A649=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(A649=\"R410A\",0.42,IF(A649=\"R407C\",0.46,IF(A649=\"R22\",0.28,\"NG\")))","v":0.42},0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2802HLXB-V  "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",{"$f":"IF(J650=\"φ6.4\",K650*L650,IF(J650=\"φ9.5\",K650*M650,IF(J650=\"φ12.7\",K650*N650,IF(J650=\"φ15.9\",K650*O650,IF(J650=\"φ19.1\",K650*P650,IF(J650=\"φ22.2\",K650*Q650,IF(J650=\"φ25.4\",K650*R650,0)))))))","v":0},null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3352HLXB-KV "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3352HLXB-V  "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4002HLXB-V  "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4502HLXB-V  "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5042HLXB-V  "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5602HLXB-V  "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6152HLXB-V  "," ",null,null,null,null,21.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,21.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6802HLXB-V  "," ",null,null,null,null,21.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,21.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2242HLXB-V "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2802HLXB-V "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3352HLXB-KV"," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3352HLXB-V "," ",null,null,null,null,14.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,14.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4002HLXB-V "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4502HLXB-V "," ",null,null,null,null,17,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,17,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5042HLXB-V "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5602HLXB-V "," ",null,null,null,null,19.399999999999999,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,19.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6152HLXB-V "," ",null,null,null,null,21.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,21.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6802HLXB-V "," ",null,null,null,null,21.2,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,0.25,0.35,"***",0,null,"その他",0,0,0,21.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP1123HLX     "," ",null,null,null,null,5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,"***","***","***","***","***",0,null,"その他",{"$f":"3.38-H669","v":-1.62},{"$f":"V669","v":-1.62},0,5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP1403HLX     "," ",null,null,null,null,5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,"***","***","***","***","***",0,null,"その他",{"$f":"3.38-H670","v":-1.62},-1.62,0,5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP1123HLX    "," ",null,null,null,null,5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,"***","***","***","***","***",0,null,"その他",{"$f":"3.38-H671","v":-1.62},-1.62,0,5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP1403HLX    "," ",null,null,null,null,5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,"***","***","***","***","***",0,null,"その他",{"$f":"3.38-H672","v":-1.62},-1.62,0,5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2243HLXY    "," ",null,null,null,null,14,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",0,0,0,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2803HLXY    "," ",null,null,null,null,14,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",0,0,0,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3353HLXY    "," ",null,null,null,null,14,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",0,0,0,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2243HLXY   "," ",null,null,null,null,14,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",0,0,0,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2803HLXY   "," ",null,null,null,null,14,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",0,0,0,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3353HLXY   "," ",null,null,null,null,14,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",0,0,0,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3353HLX-K   "," ",null,null,null,null,11.9,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,11.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4003HLX     "," ",null,null,null,null,12.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,12.8,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4503HLX     "," ",null,null,null,null,14.6,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,14.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5043HLX     "," ",null,null,null,null,16.3,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,16.3,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5603HLX     "," ",null,null,null,null,17.399999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,17.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6153HLX     "," ",null,null,null,null,18.600000000000001,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,18.600000000000001,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6803HLX     "," ",null,null,null,null,19.899999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,19.899999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP7353HLX     "," ","FDCP3353HLX-K   ","FDCP4003HLX     ",null,null,{"$f":"H679+H680","v":24.700000000000003},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,24.700000000000003,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP8003HLX     "," ","FDCP4003HLX     ","FDCP4003HLX     ",null,null,{"$f":"H680+H680","v":25.6},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,25.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP8503HLX     "," ","FDCP4003HLX     ","FDCP4503HLX     ",null,null,{"$f":"H680+H681","v":27.4},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,27.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP9003HLX     "," ","FDCP4503HLX     ","FDCP4503HLX     ",null,null,{"$f":"H681+H681","v":29.2},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,29.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP9603HLX     "," ","FDCP4503HLX     ","FDCP5043HLX     ",null,null,{"$f":"H681+H682","v":30.9},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,30.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP10103HLX     "," ","FDCP5043HLX     ","FDCP5043HLX     ",null,null,{"$f":"H682+H682","v":32.6},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,32.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP10653HLX     "," ","FDCP5043HLX     ","FDCP5603HLX     ",null,null,{"$f":"H682+H683","v":33.700000000000003},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,33.700000000000003,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP11303HLX     "," ","FDCP5603HLX     ","FDCP5603HLX     ",null,null,{"$f":"H683+H683","v":34.799999999999997},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,34.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP11803HLX     "," ","FDCP5603HLX     ","FDCP6153HLX     ",null,null,{"$f":"H683+H684","v":36},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,36,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP12353HLX     "," ","FDCP6153HLX     ","FDCP6153HLX     ",null,null,{"$f":"H684+H684","v":37.200000000000003},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,37.200000000000003,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP13003HLX     "," ","FDCP6153HLX     ","FDCP6803HLX     ",null,null,{"$f":"H684+H685","v":38.5},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,{"$f":"IF(S696+W696<0,0,S696+W696)","v":0},38.5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP13603HLX     "," ","FDCP6803HLX     ","FDCP6803HLX     ",null,null,{"$f":"H685+H685","v":39.799999999999997},100,"φ22.2",330,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",122.1,26,"その他",0,0,{"$f":"IF(S697+W697<0,0,S697+W697)","v":122.1},161.89999999999998,1.6189999999999998,0.39,0.42,0.42,"対策が２つ必要です"]
["R410A","FDCSP3353HLX-K  "," ",null,null,null,null,11.9,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,11.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4003HLX    "," ",null,null,null,null,12.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,12.8,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4503HLX    "," ",null,null,null,null,14.6,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,14.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5043HLX    "," ",null,null,null,null,16.3,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,16.3,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5603HLX    "," ",null,null,null,null,17.399999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,17.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6153HLX    "," ",null,null,null,null,18.600000000000001,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,18.600000000000001,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6803HLX    "," ",null,null,null,null,19.899999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,19.899999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP7353HLX     "," ","FDCSP3353HLX-K   ","FDCSP4003HLX     ",null,null,{"$f":"H698+H699","v":24.700000000000003},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,24.700000000000003,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP8003HLX     "," ","FDCSP4003HLX     ","FDCSP4003HLX     ",null,null,{"$f":"H699+H699","v":25.6},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,25.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP8503HLX     "," ","FDCSP4003HLX     ","FDCSP4503HLX     ",null,null,{"$f":"H699+H700","v":27.4},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,27.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP9003HLX     "," ","FDCSP4503HLX     ","FDCSP4503HLX     ",null,null,{"$f":"H700+H700","v":29.2},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,29.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP9603HLX     "," ","FDCSP4503HLX     ","FDCSP5043HLX     ",null,null,{"$f":"H700+H701","v":30.9},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,30.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP10103HLX     "," ","FDCSP5043HLX     ","FDCSP5043HLX     ",null,null,{"$f":"H701+H701","v":32.6},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,{"$f":"H710+X710","v":32.6},{"$f":"Y710/I710","v":{"$error":"#DIV/0!"}},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP10653HLX     "," ","FDCSP5043HLX     ","FDCSP5603HLX     ",null,null,{"$f":"H701+H702","v":33.700000000000003},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,33.700000000000003,{"$error":"#DIV/0!"},0.39,0.42,{"$f":"IF(A711=\"R410A\",0.42,IF(A711=\"R407C\",0.49,IF(A711=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z711<=AA711,AND(U711=\"その他\",Z711<=AB711)),\"OK\",IF(OR(AND(U711=\"最下層\",Z711<=AB711),AND(U711=\"その他\",Z711<=AC711)),\"対策が１つ必要です\",IF(OR(AND(U711=\"最下層\",Z711<=AC711),AND(U711=\"その他\",Z711>AC711)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCSP11303HLX     "," ","FDCSP5603HLX     ","FDCSP5603HLX     ",null,null,{"$f":"H702+H702","v":34.799999999999997},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,34.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP11803HLX     "," ","FDCSP5603HLX     ","FDCSP6153HLX     ",null,null,{"$f":"H702+H703","v":36},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,{"$f":"V713","v":0},{"$f":"IF(S713+W713<0,0,S713+W713)","v":0},36,{"$error":"#DIV/0!"},{"$f":"IF(A713=\"R410A\",0.39,IF(A713=\"R407C\",0.27,IF(A713=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(A713=\"R410A\",0.42,IF(A713=\"R407C\",0.46,IF(A713=\"R22\",0.28,\"NG\")))","v":0.42},0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP12353HLX     "," ","FDCSP6153HLX     ","FDCSP6153HLX     ",null,null,{"$f":"H703+H703","v":37.200000000000003},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",{"$f":"IF(J714=\"φ6.4\",K714*L714,IF(J714=\"φ9.5\",K714*M714,IF(J714=\"φ12.7\",K714*N714,IF(J714=\"φ15.9\",K714*O714,IF(J714=\"φ19.1\",K714*P714,IF(J714=\"φ22.2\",K714*Q714,IF(J714=\"φ25.4\",K714*R714,0)))))))","v":0},null,"その他",0,0,{"$f":"IF(S714+W714<0,0,S714+W714)","v":0},37.200000000000003,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP13003HLX     "," ","FDCSP6153HLX     ","FDCSP6803HLX     ",null,null,{"$f":"H703+H704","v":38.5},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",{"$f":"IF(J715=\"φ6.4\",K715*L715,IF(J715=\"φ9.5\",K715*M715,IF(J715=\"φ12.7\",K715*N715,IF(J715=\"φ15.9\",K715*O715,IF(J715=\"φ19.1\",K715*P715,IF(J715=\"φ22.2\",K715*Q715,IF(J715=\"φ25.4\",K715*R715,0)))))))","v":0},null,"その他",0,0,{"$f":"IF(S715+W715<0,0,S715+W715)","v":0},38.5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP13603HLX     "," ","FDCSP6803HLX     ","FDCSP6803HLX     ",null,null,{"$f":"H704+H704","v":39.799999999999997},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",{"$f":"IF(J716=\"φ6.4\",K716*L716,IF(J716=\"φ9.5\",K716*M716,IF(J716=\"φ12.7\",K716*N716,IF(J716=\"φ15.9\",K716*O716,IF(J716=\"φ19.1\",K716*P716,IF(J716=\"φ22.2\",K716*Q716,IF(J716=\"φ25.4\",K716*R716,0)))))))","v":0},null,"その他",0,0,{"$f":"IF(S716+W716<0,0,S716+W716)","v":0},39.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2243HLXR    "," ",null,null,null,null,8.6999999999999993,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",{"$f":"IF(J717=\"φ6.4\",K717*L717,IF(J717=\"φ9.5\",K717*M717,IF(J717=\"φ12.7\",K717*N717,IF(J717=\"φ15.9\",K717*O717,IF(J717=\"φ19.1\",K717*P717,IF(J717=\"φ22.2\",K717*Q717,IF(J717=\"φ25.4\",K717*R717,0)))))))*1.3","v":0},null,"その他",0,0,{"$f":"IF(S717+W717<0,0,S717+W717)","v":0},8.6999999999999993,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2803HLXR    "," ",null,null,null,null,9.9,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",{"$f":"IF(J718=\"φ6.4\",K718*L718,IF(J718=\"φ9.5\",K718*M718,IF(J718=\"φ12.7\",K718*N718,IF(J718=\"φ15.9\",K718*O718,IF(J718=\"φ19.1\",K718*P718,IF(J718=\"φ22.2\",K718*Q718,IF(J718=\"φ25.4\",K718*R718,0)))))))*1.3","v":0},null,"その他",0,0,0,9.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3353HLXR    "," ",null,null,null,null,11.4,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,11.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3353HLXR-K  "," ",null,null,null,null,11.9,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,11.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4003HLXR    "," ",null,null,null,null,12.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,12.8,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4503HLXR    "," ",null,null,null,null,14.6,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,14.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5043HLXR    "," ",null,null,null,null,16.3,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,16.3,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5603HLXR    "," ",null,null,null,null,17.399999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,17.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6153HLXR    "," ",null,null,null,null,18.600000000000001,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,18.600000000000001,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6803HLXR    "," ",null,null,null,null,19.899999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,19.899999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP7353HLXR    "," ","FDCP3353HLXR-K  ","FDCP4003HLXR    ",null,null,{"$f":"H720+H721","v":24.700000000000003},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",{"$f":"IF(J727=\"φ6.4\",K727*L727,IF(J727=\"φ9.5\",K727*M727,IF(J727=\"φ12.7\",K727*N727,IF(J727=\"φ15.9\",K727*O727,IF(J727=\"φ19.1\",K727*P727,IF(J727=\"φ22.2\",K727*Q727,IF(J727=\"φ25.4\",K727*R727,0)))))))*1.2","v":0},null,"その他",0,0,0,24.700000000000003,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP8003HLXR    "," ","FDCP4003HLXR    ","FDCP4003HLXR    ",null,null,{"$f":"H721+H721","v":25.6},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",{"$f":"IF(J728=\"φ6.4\",K728*L728,IF(J728=\"φ9.5\",K728*M728,IF(J728=\"φ12.7\",K728*N728,IF(J728=\"φ15.9\",K728*O728,IF(J728=\"φ19.1\",K728*P728,IF(J728=\"φ22.2\",K728*Q728,IF(J728=\"φ25.4\",K728*R728,0)))))))*1.2","v":0},null,"その他",0,0,0,25.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP8503HLXR    "," ","FDCP4003HLXR    ","FDCP4503HLXR    ",null,null,{"$f":"H721+H722","v":27.4},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,27.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP9003HLXR    "," ","FDCP4503HLXR    ","FDCP4503HLXR    ",null,null,{"$f":"H722+H722","v":29.2},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,29.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP9603HLXR    "," ","FDCP4503HLXR    ","FDCP5043HLXR    ",null,null,{"$f":"H722+H723","v":30.9},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,30.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP10103HLXR    "," ","FDCP5043HLXR    ","FDCP5043HLXR    ",null,null,{"$f":"H723+H723","v":32.6},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,32.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP10653HLXR    "," ","FDCP5043HLXR    ","FDCP5603HLXR    ",null,null,{"$f":"H723+H724","v":33.700000000000003},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,33.700000000000003,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP11303HLXR    "," ","FDCP5603HLXR    ","FDCP5603HLXR    ",null,null,{"$f":"H724+H724","v":34.799999999999997},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,34.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP11803HLXR    "," ","FDCP5603HLXR    ","FDCP6153HLXR    ",null,null,{"$f":"H724+H725","v":36},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,36,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP12353HLXR    "," ","FDCP6153HLXR    ","FDCP6153HLXR    ",null,null,{"$f":"H725+H725","v":37.200000000000003},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,37.200000000000003,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP13003HLXR    "," ","FDCP6153HLXR    ","FDCP6803HLXR    ",null,null,{"$f":"H725+H726","v":38.5},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,38.5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP13603HLXR    "," ","FDCP6803HLXR    ","FDCP6803HLXR    ",null,null,{"$f":"H726+H726","v":39.799999999999997},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,39.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2243HLXR   "," ",null,null,null,null,8.6999999999999993,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",{"$f":"IF(J739=\"φ6.4\",K739*L739,IF(J739=\"φ9.5\",K739*M739,IF(J739=\"φ12.7\",K739*N739,IF(J739=\"φ15.9\",K739*O739,IF(J739=\"φ19.1\",K739*P739,IF(J739=\"φ22.2\",K739*Q739,IF(J739=\"φ25.4\",K739*R739,0)))))))*1.3","v":0},null,"その他",0,0,0,8.6999999999999993,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2803HLXR   "," ",null,null,null,null,9.9,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",{"$f":"IF(J740=\"φ6.4\",K740*L740,IF(J740=\"φ9.5\",K740*M740,IF(J740=\"φ12.7\",K740*N740,IF(J740=\"φ15.9\",K740*O740,IF(J740=\"φ19.1\",K740*P740,IF(J740=\"φ22.2\",K740*Q740,IF(J740=\"φ25.4\",K740*R740,0)))))))*1.3","v":0},null,"その他",0,0,0,9.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3353HLXR   "," ",null,null,null,null,11.4,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,11.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3353HLXR-K "," ",null,null,null,null,11.9,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,11.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4003HLXR   "," ",null,null,null,null,12.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,12.8,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4503HLXR   "," ",null,null,null,null,14.6,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,14.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5043HLXR   "," ",null,null,null,null,16.3,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,16.3,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5603HLXR   "," ",null,null,null,null,17.399999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,17.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6153HLXR   "," ",null,null,null,null,18.600000000000001,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,18.600000000000001,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6803HLXR   "," ",null,null,null,null,19.899999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,19.899999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP7353HLXR    "," ","FDCSP3353HLXR-K  ","FDCSP4003HLXR    ",null,null,{"$f":"H742+H743","v":24.700000000000003},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",{"$f":"IF(J749=\"φ6.4\",K749*L749,IF(J749=\"φ9.5\",K749*M749,IF(J749=\"φ12.7\",K749*N749,IF(J749=\"φ15.9\",K749*O749,IF(J749=\"φ19.1\",K749*P749,IF(J749=\"φ22.2\",K749*Q749,IF(J749=\"φ25.4\",K749*R749,0)))))))*1.2","v":0},null,"その他",0,0,0,24.700000000000003,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP8003HLXR    "," ","FDCSP4003HLXR    ","FDCSP4003HLXR    ",null,null,{"$f":"H743+H743","v":25.6},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",{"$f":"IF(J750=\"φ6.4\",K750*L750,IF(J750=\"φ9.5\",K750*M750,IF(J750=\"φ12.7\",K750*N750,IF(J750=\"φ15.9\",K750*O750,IF(J750=\"φ19.1\",K750*P750,IF(J750=\"φ22.2\",K750*Q750,IF(J750=\"φ25.4\",K750*R750,0)))))))*1.2","v":0},null,"その他",0,0,0,25.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP8503HLXR    "," ","FDCSP4003HLXR    ","FDCSP4503HLXR    ",null,null,{"$f":"H743+H744","v":27.4},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,27.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP9003HLXR    "," ","FDCSP4503HLXR    ","FDCSP4503HLXR    ",null,null,{"$f":"H744+H744","v":29.2},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,29.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP9603HLXR    "," ","FDCSP4503HLXR    ","FDCSP5043HLXR    ",null,null,{"$f":"H744+H745","v":30.9},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,30.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP10103HLXR    "," ","FDCSP5043HLXR    ","FDCSP5043HLXR    ",null,null,{"$f":"H745+H745","v":32.6},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,32.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP10653HLXR    "," ","FDCSP5043HLXR    ","FDCSP5603HLXR    ",null,null,{"$f":"H745+H746","v":33.700000000000003},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,33.700000000000003,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP11303HLXR    "," ","FDCSP5603HLXR    ","FDCSP5603HLXR    ",null,null,{"$f":"H746+H746","v":34.799999999999997},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,34.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP11803HLXR    "," ","FDCSP5603HLXR    ","FDCSP6153HLXR    ",null,null,{"$f":"H746+H747","v":36},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,36,{"$error":"#DIV/0!"},0.39,0.42,{"$f":"IF(A757=\"R410A\",0.42,IF(A757=\"R407C\",0.49,IF(A757=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z757<=AA757,AND(U757=\"その他\",Z757<=AB757)),\"OK\",IF(OR(AND(U757=\"最下層\",Z757<=AB757),AND(U757=\"その他\",Z757<=AC757)),\"対策が１つ必要です\",IF(OR(AND(U757=\"最下層\",Z757<=AC757),AND(U757=\"その他\",Z757>AC757)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCSP12353HLXR    "," ","FDCSP6153HLXR    ","FDCSP6153HLXR    ",null,null,{"$f":"H747+H747","v":37.200000000000003},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,37.200000000000003,{"$error":"#DIV/0!"},0.39,0.42,{"$f":"IF(A758=\"R410A\",0.42,IF(A758=\"R407C\",0.49,IF(A758=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z758<=AA758,AND(U758=\"その他\",Z758<=AB758)),\"OK\",IF(OR(AND(U758=\"最下層\",Z758<=AB758),AND(U758=\"その他\",Z758<=AC758)),\"対策が１つ必要です\",IF(OR(AND(U758=\"最下層\",Z758<=AC758),AND(U758=\"その他\",Z758>AC758)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCSP13003HLXR    "," ","FDCSP6153HLXR    ","FDCSP6803HLXR    ",null,null,{"$f":"H747+H748","v":38.5},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,38.5,{"$error":"#DIV/0!"},0.39,0.42,{"$f":"IF(A759=\"R410A\",0.42,IF(A759=\"R407C\",0.49,IF(A759=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z759<=AA759,AND(U759=\"その他\",Z759<=AB759)),\"OK\",IF(OR(AND(U759=\"最下層\",Z759<=AB759),AND(U759=\"その他\",Z759<=AC759)),\"対策が１つ必要です\",IF(OR(AND(U759=\"最下層\",Z759<=AC759),AND(U759=\"その他\",Z759>AC759)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCSP13603HLXR    "," ","FDCSP6803HLXR    ","FDCSP6803HLXR    ",null,null,{"$f":"H748+H748","v":39.799999999999997},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,39.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,{"$f":"IF(A760=\"R410A\",0.42,IF(A760=\"R407C\",0.49,IF(A760=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z760<=AA760,AND(U760=\"その他\",Z760<=AB760)),\"OK\",IF(OR(AND(U760=\"最下層\",Z760<=AB760),AND(U760=\"その他\",Z760<=AC760)),\"対策が１つ必要です\",IF(OR(AND(U760=\"最下層\",Z760<=AC760),AND(U760=\"その他\",Z760>AC760)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCRP2243HLXY   "," ",null,null,null,null,14,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",{"$f":"IF(J761=\"φ6.4\",K761*L761,IF(J761=\"φ9.5\",K761*M761,IF(J761=\"φ12.7\",K761*N761,IF(J761=\"φ15.9\",K761*O761,IF(J761=\"φ19.1\",K761*P761,IF(J761=\"φ22.2\",K761*Q761,IF(J761=\"φ25.4\",K761*R761,0)))))))","v":0},null,"その他",0,0,0,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP2803HLXY   "," ",null,null,null,null,14,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",{"$f":"IF(J762=\"φ6.4\",K762*L762,IF(J762=\"φ9.5\",K762*M762,IF(J762=\"φ12.7\",K762*N762,IF(J762=\"φ15.9\",K762*O762,IF(J762=\"φ19.1\",K762*P762,IF(J762=\"φ22.2\",K762*Q762,IF(J762=\"φ25.4\",K762*R762,0)))))))","v":0},null,"その他",0,{"$f":"V762","v":0},{"$f":"IF(S762+W762<0,0,S762+W762)","v":0},14,{"$error":"#DIV/0!"},{"$f":"IF(A762=\"R410A\",0.39,IF(A762=\"R407C\",0.27,IF(A762=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(A762=\"R410A\",0.42,IF(A762=\"R407C\",0.46,IF(A762=\"R22\",0.28,\"NG\")))","v":0.42},{"$f":"IF(A762=\"R410A\",0.42,IF(A762=\"R407C\",0.49,IF(A762=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z762<=AA762,AND(U762=\"その他\",Z762<=AB762)),\"OK\",IF(OR(AND(U762=\"最下層\",Z762<=AB762),AND(U762=\"その他\",Z762<=AC762)),\"対策が１つ必要です\",IF(OR(AND(U762=\"最下層\",Z762<=AC762),AND(U762=\"その他\",Z762>AC762)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCRP2803HLX-K  "," ",null,null,null,null,10.4,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,10.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP3353HLX    "," ",null,null,null,null,11.9,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,11.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP4003HLX    "," ",null,null,null,null,12.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,12.8,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP4503HLX    "," ",null,null,null,null,14.6,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,14.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP5043HLX    "," ",null,null,null,null,17.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,17.8,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP5603HLX    "," ",null,null,null,null,18.899999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,18.899999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP6153HLX    "," ","FDCRP2803HLX-K  ","FDCRP3353HLX    ",null,null,{"$f":"H763+H764","v":22.3},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,22.3,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP6803HLX    "," ","FDCRP3353HLX    ","FDCRP3353HLX    ",null,null,{"$f":"H764+H764","v":23.8},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,23.8,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP7353HLX    "," ","FDCRP3353HLX    ","FDCRP4003HLX    ",null,null,{"$f":"H764+H765","v":24.700000000000003},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,24.700000000000003,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP8003HLX    "," ","FDCRP4003HLX    ","FDCRP4003HLX    ",null,null,{"$f":"H765+H765","v":25.6},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,25.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP8503HLX    "," ","FDCRP4003HLX    ","FDCRP4503HLX    ",null,null,{"$f":"H765+H766","v":27.4},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,27.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP9003HLX    "," ","FDCRP4503HLX    ","FDCRP4503HLX    ",null,null,{"$f":"H766+H766","v":29.2},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,{"$f":"H774+X774","v":29.2},{"$f":"Y774/I774","v":{"$error":"#DIV/0!"}},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP9603HLX    "," ","FDCRP4503HLX    ","FDCRP5043HLX    ",null,null,{"$f":"H766+H767","v":32.4},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,32.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$f":"IF(OR(Z775<=AA775,AND(U775=\"その他\",Z775<=AB775)),\"OK\",IF(OR(AND(U775=\"最下層\",Z775<=AB775),AND(U775=\"その他\",Z775<=AC775)),\"対策が１つ必要です\",IF(OR(AND(U775=\"最下層\",Z775<=AC775),AND(U775=\"その他\",Z775>AC775)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCRP10103HLX    "," ","FDCRP5043HLX    ","FDCRP5043HLX    ",null,null,{"$f":"H767+H767","v":35.6},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,35.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP2243HLXY  "," ",null,null,null,null,14,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",0,{"$f":"V777","v":0},0,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP2803HLXY  "," ",null,null,null,null,14,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",0,{"$f":"V778","v":0},{"$f":"IF(S778+W778<0,0,S778+W778)","v":0},14,{"$error":"#DIV/0!"},{"$f":"IF(A778=\"R410A\",0.39,IF(A778=\"R407C\",0.27,IF(A778=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(A778=\"R410A\",0.42,IF(A778=\"R407C\",0.46,IF(A778=\"R22\",0.28,\"NG\")))","v":0.42},{"$f":"IF(A778=\"R410A\",0.42,IF(A778=\"R407C\",0.49,IF(A778=\"R22\",0.5,\"NG\")))","v":0.42},{"$f":"IF(OR(Z778<=AA778,AND(U778=\"その他\",Z778<=AB778)),\"OK\",IF(OR(AND(U778=\"最下層\",Z778<=AB778),AND(U778=\"その他\",Z778<=AC778)),\"対策が１つ必要です\",IF(OR(AND(U778=\"最下層\",Z778<=AC778),AND(U778=\"その他\",Z778>AC778)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCRSP2803HLX-K "," ",null,null,null,null,10.4,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,10.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP3353HLX   "," ",null,null,null,null,11.9,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,11.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP4003HLX   "," ",null,null,null,null,12.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,{"$f":"IF(S781+W781<0,0,S781+W781)","v":0},12.8,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP4503HLX   "," ",null,null,null,null,14.6,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,14.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP5043HLX   "," ",null,null,null,null,17.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,17.8,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP5603HLX   "," ",null,null,null,null,18.899999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,18.899999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP6153HLX    "," ","FDCRSP2803HLX-K  ","FDCRSP3353HLX    ",null,null,{"$f":"H780+H781","v":24.700000000000003},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,24.700000000000003,{"$error":"#DIV/0!"},0.39,0.42,{"$f":"IF(A785=\"R410A\",0.42,IF(A785=\"R407C\",0.49,IF(A785=\"R22\",0.5,\"NG\")))","v":0.42},{"$error":"#DIV/0!"}]
["R410A","FDCRSP6803HLX    "," ","FDCRSP3353HLX    ","FDCRSP3353HLX    ",null,null,{"$f":"H781+H781","v":25.6},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,25.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP7353HLX    "," ","FDCRSP3353HLX    ","FDCRSP4003HLX    ",null,null,{"$f":"H781+H782","v":27.4},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,27.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP8003HLX    "," ","FDCRSP4003HLX    ","FDCRSP4003HLX    ",null,null,{"$f":"H782+H782","v":29.2},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,29.2,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP8503HLX    "," ","FDCRSP4003HLX    ","FDCRSP4503HLX    ",null,null,{"$f":"H782+H783","v":32.4},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,32.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP9003HLX    "," ","FDCRSP4503HLX    ","FDCRSP4503HLX    ",null,null,{"$f":"H783+H783","v":35.6},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,35.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP9603HLX    "," ","FDCRSP4503HLX    ","FDCRSP5043HLX    ",null,null,{"$f":"H783+H784","v":36.700000000000003},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,36.700000000000003,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP10103HLX    "," ","FDCRSP5043HLX    ","FDCRSP5043HLX    ",null,null,{"$f":"H784+H784","v":37.799999999999997},null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,37.799999999999997,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP1603HLXYA   "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2243HLXYA   "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2803HLXYA   "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3353HLXYA   "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP2243HLXYA  "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP2803HLXYA  "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP2243HLXYA "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP2803HLXYA "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP1603HLXYA  "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2243HLXYA  "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2803HLXYA  "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3353HLXYA  "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP1123HLX     ","A",null,null,null,null,5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,"***","***","***","***","***",0,null,"その他",{"$f":"3.38-H805","v":-1.62},-1.62,0,5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP1403HLX     ","A",null,null,null,null,5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,"***","***","***","***","***",0,null,"その他",{"$f":"3.38-H806","v":-1.62},-1.62,0,5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP1123HLX    ","A",null,null,null,null,5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,"***","***","***","***","***",0,null,"その他",{"$f":"3.38-H807","v":-1.62},-1.62,0,5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP1403HLX    ","A",null,null,null,null,5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,"***","***","***","***","***",0,null,"その他",{"$f":"3.38-H808","v":-1.62},-1.62,0,5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP2803HLX-K  ","T",null,null,null,null,10.4,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,10.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP1603HLX     "," ",null,null,null,null,5.34,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,"***","***","***","***","***",0,null,"その他",0,0,0,5.34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP1603HLX    "," ",null,null,null,null,5.34,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,"***","***","***","***","***",0,null,"その他",0,0,0,5.34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP2803HLXA-K "," ",null,null,null,null,10.4,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,10.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP3353HLXA   "," ",null,null,null,null,11.9,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,11.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP4003HLXA   "," ",null,null,null,null,12.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,12.8,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP4503HLXA   "," ",null,null,null,null,14.6,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,14.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP5043HLXA   "," ",null,null,null,null,17.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,17.8,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP5603HLXA   "," ",null,null,null,null,18.899999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,18.899999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP2803HLXA-K"," ",null,null,null,null,10.4,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,10.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP3353HLXA  "," ",null,null,null,null,11.9,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,11.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP4003HLXA  "," ",null,null,null,null,12.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,12.8,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP4503HLXA  "," ",null,null,null,null,14.6,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,14.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP5043HLXA  "," ",null,null,null,null,17.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,17.8,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP5603HLXA  "," ",null,null,null,null,18.899999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,18.899999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP1123HLXB    "," ",null,null,null,null,5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,"***","***","***","***","***",0,null,"その他",{"$f":"3.38-H824","v":-1.62},-1.62,0,5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP1403HLXB    "," ",null,null,null,null,5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,"***","***","***","***","***",0,null,"その他",{"$f":"3.38-H825","v":-1.62},-1.62,0,5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP1603HLXB    "," ",null,null,null,null,5.34,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,"***","***","***","***","***",{"$f":"IF(J826=\"φ6.4\",K826*L826,IF(J826=\"φ9.5\",K826*M826,IF(J826=\"φ12.7\",K826*N826,IF(J826=\"φ15.9\",K826*O826,IF(J826=\"φ19.1\",K826*P826,IF(J826=\"φ22.2\",K826*Q826,IF(J826=\"φ25.4\",K826*R826,0)))))))","v":0},null,"その他",0,0,0,5.34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3353HLXB-K  "," ",null,null,null,null,11.9,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,11.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4003HLXB    "," ",null,null,null,null,12.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,12.8,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP4503HLXB    "," ",null,null,null,null,14.6,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,14.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5043HLXB    "," ",null,null,null,null,16.3,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,16.3,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP5603HLXB    "," ",null,null,null,null,17.399999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,17.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6153HLXB    "," ",null,null,null,null,18.600000000000001,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,18.600000000000001,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP6803HLXB    "," ",null,null,null,null,19.899999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,19.899999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP2803HLXB-K "," ",null,null,null,null,10.4,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,10.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP3353HLXB   "," ",null,null,null,null,11.9,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,11.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP4003HLXB   "," ",null,null,null,null,12.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,12.8,{"$error":"#DIV/0!"},{"$f":"IF(A836=\"R410A\",0.39,IF(A836=\"R407C\",0.27,IF(A836=\"R22\",0.21,\"NG\")))","v":0.39},{"$f":"IF(A836=\"R410A\",0.42,IF(A836=\"R407C\",0.46,IF(A836=\"R22\",0.28,\"NG\")))","v":0.42},0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP4503HLXB   "," ",null,null,null,null,14.6,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,14.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP5043HLXB   "," ",null,null,null,null,17.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,{"$f":"H838+X838","v":17.8},{"$f":"Y838/I838","v":{"$error":"#DIV/0!"}},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP5603HLXB   "," ",null,null,null,null,18.899999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,18.899999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$f":"IF(OR(Z839<=AA839,AND(U839=\"その他\",Z839<=AB839)),\"OK\",IF(OR(AND(U839=\"最下層\",Z839<=AB839),AND(U839=\"その他\",Z839<=AC839)),\"対策が１つ必要です\",IF(OR(AND(U839=\"最下層\",Z839<=AC839),AND(U839=\"その他\",Z839>AC839)),\"対策が２つ必要です\",\"システムの見直しが必要です\")))","v":{"$error":"#DIV/0!"}}]
["R410A","FDCRSP2803HLXB-K"," ",null,null,null,null,10.4,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,10.4,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP3353HLXB  "," ",null,null,null,null,11.9,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,{"$f":"V841","v":0},0,11.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP4003HLXB  "," ",null,null,null,null,12.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,12.8,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP4503HLXB  "," ",null,null,null,null,14.6,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,14.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP5043HLXB  "," ",null,null,null,null,17.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,17.8,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP5603HLXB  "," ",null,null,null,null,18.899999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,{"$f":"IF(S845+W845<0,0,S845+W845)","v":0},18.899999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP1123HLXB   "," ",null,null,null,null,5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,"***","***","***","***","***",0,null,"その他",{"$f":"3.38-H846","v":-1.62},{"$f":"V846","v":-1.62},{"$f":"IF(S846+W846<0,0,S846+W846)","v":0},5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP1403HLXB   "," ",null,null,null,null,5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,"***","***","***","***","***",0,null,"その他",{"$f":"3.38-H847","v":-1.62},-1.62,{"$f":"IF(S847+W847<0,0,S847+W847)","v":0},5,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP1603HLXB   "," ",null,null,null,null,5.34,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,"***","***","***","***","***",0,null,"その他",0,0,{"$f":"IF(S848+W848<0,0,S848+W848)","v":0},5.34,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3353HLXB-K "," ",null,null,null,null,11.9,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,11.9,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4003HLXB   "," ",null,null,null,null,12.8,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,12.8,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP4503HLXB   "," ",null,null,null,null,14.6,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,14.6,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5043HLXB   "," ",null,null,null,null,16.3,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,16.3,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP5603HLXB   "," ",null,null,null,null,17.399999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,17.399999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6153HLXB   "," ",null,null,null,null,18.600000000000001,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,18.600000000000001,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP6803HLXB   "," ",null,null,null,null,19.899999999999999,null,null,null,2.1999999999999999E-2,5.8999999999999997E-2,0.12,0.18,0.26,0.37,"***",0,null,"その他",0,0,0,19.899999999999999,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2243HLXYB   "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP2803HLXYB   "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCP3353HLXYB   "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP2243HLXYB  "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRP2803HLXYB  "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP2243HLXYB "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCRSP2803HLXYB "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2243HLXYB  "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP2803HLXYB  "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]
["R410A","FDCSP3353HLXYB  "," ",null,null,null,null,11.5,null,null,null,2.1999999999999999E-2,5.3999999999999999E-2,0.11,0.17,"***","***","***",0,null,"その他",2.5,2.5,2.5,14,{"$error":"#DIV/0!"},0.39,0.42,0.42,{"$error":"#DIV/0!"}]

{"sheet":"ルックアップ用の表","index":4,"n_rows":44,"n_cols":14,"rows_kept":44,"cut":false,"hidden":true,"merged":[]}
[1,2,3,4,5,6,null,null,1,2,3,4,5]
["関数用","型","標準・ﾘﾌﾚｯｼｭ\n冷暖ﾌﾘｰ・寒冷地","室外機\n馬力","実長\n90m未満","実長\n90m以上","備考",null,"関数用","型","標準・ﾘﾌﾚｯｼｭ\n冷暖ﾌﾘｰ・寒冷地","室外機\n馬力","一系統封入量\n上限","備考"]
[{"$f":"B3&C3&\",\"&D3","v":"R32標準,4"},"R32","標準",4,9.52,"***",null,null,{"$f":"J3&K3&\",\"&L3","v":"LXZ標準,4"},"LXZ","標準",4,50,"関数でエラーを出さないため便宜上50と入力"]
[{"$f":"B4&C4&\",\"&D4","v":"R32標準,5"},"R32","標準",5,9.52,"***",null,null,"LXZ標準,5","LXZ","標準",5,50,"関数でエラーを出さないため便宜上50と入力"]
["R32標準,6","R32","標準",6,9.52,"***",null,null,"LXZ標準,6","LXZ","標準",6,50,"関数でエラーを出さないため便宜上50と入力"]
["R32標準,8","R32","標準",8,9.52,12.7,null,null,"LXZY標準,8","LXZY","標準",8,50,"関数でエラーを出さないため便宜上50と入力"]
["R32標準,10","R32","標準",10,9.52,12.7,null,null,"LXZY標準,10","LXZY","標準",10,50,"関数でエラーを出さないため便宜上50と入力"]
[{"$f":"B8&C8&\",\"&D8","v":"R32標準,8"},"R32","標準",8,9.52,12.7,null,null,{"$f":"J8&K8&\",\"&L8","v":"LXZ標準,8"},"LXZ","標準",8,63.8,"関数でエラーを出さないため便宜上51と入力"]
["R32標準,10","R32","標準",10,9.52,12.7,null,null,"LXZ標準,10","LXZ","標準",10,63.8,"マルチカタログ10年7月版108ページ"]
["R32標準,12","R32","標準",12,12.7,12.7,null,null,"LXZ標準,12","LXZ","標準",12,63.8]
["R32標準,14","R32","標準",14,12.7,12.7,null,null,"LXZ標準,14","LXZ","標準",14,63.8]
["R32標準,16","R32","標準",16,12.7,12.7,null,null,"LXZ標準,16","LXZ","標準",16,63.8]
["R32標準,18","R32","標準",18,12.7,15.88,null,null,"LXZ標準,18","LXZ","標準",18,63.8]
["R32標準,20","R32","標準",20,12.7,15.88,null,null,"LXZ標準,20","LXZ","標準",20,63.8]
["R32標準,22","R32","標準",22,12.7,15.88,null,null,"LXZ標準,22","LXZ","標準",22,63.8]
["R32標準,24","R32","標準",24,12.7,15.88,null,null,"LXZ標準,24","LXZ","標準",24,63.8]
["R32標準,26","R32","標準",26,15.88,19.05,null,null,"LXZ標準,26","LXZ","標準",26,63.8]
["R32標準,28","R32","標準",28,15.88,19.05,null,null,"LXZ標準,28","LXZ","標準",28,63.8]
["R32標準,30","R32","標準",30,15.88,19.05,null,null,"LXZ標準,30","LXZ","標準",30,63.8]
["R32標準,32","R32","標準",32,15.88,19.05,null,null,"LXZ標準,32","LXZ","標準",32,63.8]
["R32標準,34","R32","標準",34,15.88,19.05,null,null,"LXZ標準,34","LXZ","標準",34,63.8]
["R32標準,36","R32","標準",36,15.88,19.05,null,null,"LXZ標準,36","LXZ","標準",36,63.8]
["R32標準,38","R32","標準",38,19.05,22.22,null,null,"LXZ標準,38","LXZ","標準",38,63.8]
["R32標準,40","R32","標準",40,19.05,22.22,null,null,"LXZ標準,40","LXZ","標準",40,63.8]
["R32標準,42","R32","標準",42,19.05,22.22,null,null,"LXZ標準,42","LXZ","標準",42,63.8]
["R32標準,44","R32","標準",44,19.05,22.22,null,null,"LXZ標準,44","LXZ","標準",44,63.8]
["R32標準,46","R32","標準",46,19.05,22.22,null,null,"LXZ標準,46","LXZ","標準",46,63.8]
[{"$f":"B28&C28&\",\"&D28","v":"R32標準,48"},"R32","標準",48,19.05,22.22,null,null,"LXZ標準,48","LXZ","標準",48,63.8]
[{"$f":"B29&C29&\",\"&D29","v":"R32標準,54"},"R32","標準",54,19.05,22.22,null,null,"LXZ標準,54","LXZ","標準",54,63.8]
[{"$f":"B30&C30&\",\"&D30","v":"R32標準,12"},"R32","標準",12,12.7,12.7,null,null,{"$f":"J30&K30&\",\"&L30","v":"LXZ標準,12"},"LXZ","標準",12,63.8]
["R32標準,18","R32","標準",18,12.7,15.88,null,null,"LXZ標準,18","LXZ","標準",18,63.8]
["R32標準,22","R32","標準",22,12.7,15.88,null,null,"LXZ標準,22","LXZ","標準",22,63.8]
["R32標準,24","R32","標準",24,12.7,15.88,null,null,"LXZ標準,24","LXZ","標準",24,63.8]
[{"$f":"B34&C34&\",\"&D34","v":"R32標準,26"},"R32","標準",26,15.88,19.05,null,null,"LXZ標準,26","LXZ","標準",26,63.8]
["R32標準,34","R32","標準",34,15.88,19.05,null,null,"LXZ標準,34","LXZ","標準",34,63.8]
["R32標準,36","R32","標準",36,15.88,19.05,null,null,"LXZ標準,36","LXZ","標準",36,63.8]
["R32標準,38","R32","標準",38,19.05,22.22,null,null,"LXZ標準,38","LXZ","標準",38,63.8]
["R32標準,42","R32","標準",42,19.05,22.22,null,null,"LXZ標準,42","LXZ","標準",42,63.8]
["R32標準,44","R32","標準",44,19.05,22.22,null,null,"LXZ標準,44","LXZ","標準",44,63.8]
["R32標準,46","R32","標準",46,19.05,22.22,null,null,"LXZ標準,46","LXZ","標準",46,63.8]
["R32標準,48","R32","標準",48,19.05,22.22,null,null,"LXZ標準,48","LXZ","標準",48,63.8]
["R32標準,50","R32","標準",50,19.05,22.22,null,null,"LXZ標準,50","LXZ","標準",50,63.8]
["R32標準,52","R32","標準",52,19.05,22.22,null,null,"LXZ標準,52","LXZ","標準",52,63.8]
["R32標準,54","R32","標準",54,19.05,22.22,null,null,"LXZ標準,54","LXZ","標準",54,63.8]

{"sheet":"ルックアップ用の表 (2)","index":5,"n_rows":296,"n_cols":14,"rows_kept":296,"cut":false,"hidden":true,"merged":[]}
[1,2,3,4,5,6,null,null,1,2,3,4,5]
["関数用","型","標準・ﾘﾌﾚｯｼｭ\n冷暖ﾌﾘｰ・寒冷地","室外機\n馬力","実長\n90m未満","実長\n90m以上","備考",null,"関数用","型","標準・ﾘﾌﾚｯｼｭ\n冷暖ﾌﾘｰ・寒冷地","室外機\n馬力","一系統封入量\n上限","備考"]
[{"$f":"B3&C3&\",\"&D3","v":"R410A標準,4"},"R410A","標準",4,9.52,"***","マルチカタログ10年7月版103ページ",null,{"$f":"J3&K3&\",\"&L3","v":"LX3標準,4"},"LX3","標準",4,50,"関数でエラーを出さないため便宜上50と入力"]
["R410A標準,5","R410A","標準",5,9.52,"***",null,null,"LX3標準,5","LX3","標準",5,50,"関数でエラーを出さないため便宜上50と入力"]
["R410A標準,6","R410A","標準",6,9.52,"***",null,null,"LX3標準,6","LX3","標準",6,50,"関数でエラーを出さないため便宜上50と入力"]
["R410A標準,8","R410A","標準",8,9.52,12.7,null,null,"LX3標準,8","LX3","標準",8,50,"関数でエラーを出さないため便宜上50と入力"]
["R410A標準,10","R410A","標準",10,9.52,12.7,null,null,"LX3標準,10","LX3","標準",10,50,"関数でエラーを出さないため便宜上50と入力"]
[{"$f":"B8&C8&\",\"&D8","v":"R410A標準,12"},"R410A","標準",12,12.7,12.7,null,null,{"$f":"J8&K8&\",\"&L8","v":"LX3標準,12"},"LX3","標準",12,50,"関数でエラーを出さないため便宜上51と入力"]
["R410A標準,13","R410A","標準",13,12.7,12.7,null,null,"LX3標準,14","LX3","標準",14,50,"マルチカタログ10年7月版108ページ"]
["R410A標準,14","R410A","標準",14,12.7,12.7,"マルチカタログ10年7月版104ページ",null,"LX3標準,16","LX3","標準",16,50]
["R410A標準,16","R410A","標準",16,12.7,12.7,null,null,"LX3標準,18","LX3","標準",18,50]
["R410A標準,18","R410A","標準",18,12.7,15.88,null,null,"LX3標準,20","LX3","標準",20,50]
["R410A標準,20","R410A","標準",20,12.7,15.88,null,null,"LX3標準,22","LX3","標準",22,50]
["R410A標準,22","R410A","標準",22,12.7,15.88,null,null,"LX3標準,24","LX3","標準",24,50]
["R410A標準,24","R410A","標準",24,12.7,15.88,null,null,"LX3標準,26","LX3","標準",26,100]
["R410A標準,26","R410A","標準",26,15.88,19.05,null,null,"LX3標準,28","LX3","標準",28,100]
["R410A標準,28","R410A","標準",28,15.88,19.05,null,null,"LX3標準,30","LX3","標準",30,100]
["R410A標準,30","R410A","標準",30,15.88,19.05,null,null,"LX3標準,32","LX3","標準",32,100]
["R410A標準,32","R410A","標準",32,15.88,19.05,null,null,"LX3標準,34","LX3","標準",34,100]
["R410A標準,34","R410A","標準",34,15.88,19.05,null,null,"LX3標準,36","LX3","標準",36,100]
["R410A標準,36","R410A","標準",36,15.88,19.05,null,null,"LX3標準,38","LX3","標準",38,100]
["R410A標準,38","R410A","標準",38,19.05,22.22,null,null,"LX3標準,40","LX3","標準",40,100]
["R410A標準,40","R410A","標準",40,19.05,22.22,null,null,"LX3標準,42","LX3","標準",42,100]
["R410A標準,42","R410A","標準",42,19.05,22.22,null,null,"LX3標準,44","LX3","標準",44,100]
["R410A標準,44","R410A","標準",44,19.05,22.22,null,null,"LX3標準,46","LX3","標準",46,100]
["R410A標準,46","R410A","標準",46,19.05,22.22,null,null,"LX3標準,48","LX3","標準",48,100]
["R410A標準,48","R410A","標準",48,19.05,22.22,null,null,"LX3寒冷地,6","LX3","寒冷地",6,50,"関数でエラーを出さないため便宜上50と入力"]
[{"$f":"B28&C28&\",\"&D28","v":"R410A標準,50"},"R410A","標準",50,19.05,22.22,null,null,"LX3寒冷地,8","LX3","寒冷地",8,50,"関数でエラーを出さないため便宜上50と入力"]
[{"$f":"B29&C29&\",\"&D29","v":"R410A標準,52"},"R410A","標準",52,19.05,22.22,null,null,"LX3寒冷地,10","LX3","寒冷地",10,50,"関数でエラーを出さないため便宜上50と入力"]
[{"$f":"B30&C30&\",\"&D30","v":"R410A標準,54"},"R410A","標準",54,19.05,22.22,null,null,"LX3リフレッシュ,8","LX3","リフレッシュ",8,50,"関数でエラーを出さないため便宜上50と入力"]
["R410A寒冷地,6","R410A","寒冷地",6,9.52,12.7,null,null,"LX3リフレッシュ,10","LX3","リフレッシュ",10,50,"関数でエラーを出さないため便宜上50と入力"]
["R410A寒冷地,8","R410A","寒冷地",8,9.52,12.7,null,null,"LX3リフレッシュ,12","LX3","リフレッシュ",12,50,"関数でエラーを出さないため便宜上50と入力"]
["R410A寒冷地,10","R410A","寒冷地",10,9.52,12.7,null,null,"LX3リフレッシュ,14","LX3","リフレッシュ",14,50,"マルチカタログ10年7月版108ページ"]
["R410Aリフレッシュ,8","R410A","リフレッシュ",8,15.88,15.88,null,null,"LX3リフレッシュ,16","LX3","リフレッシュ",16,50]
["R410Aリフレッシュ,10","R410A","リフレッシュ",10,15.88,15.88,null,null,"LX3リフレッシュ,18","LX3","リフレッシュ",18,50]
["R410Aリフレッシュ,12","R410A","リフレッシュ",12,15.88,15.88,null,null,"LX3リフレッシュ,20","LX3","リフレッシュ",20,50]
["R410Aリフレッシュ,14","R410A","リフレッシュ",14,15.88,15.88,null,null,"LX3リフレッシュ,22","LX3","リフレッシュ",22,50]
["R410Aリフレッシュ,16","R410A","リフレッシュ",16,15.88,15.88,null,null,"LX3リフレッシュ,24","LX3","リフレッシュ",24,50]
["R410Aリフレッシュ,18","R410A","リフレッシュ",18,19.05,19.05,null,null,"LX3リフレッシュ,26","LX3","リフレッシュ",26,100]
["R410Aリフレッシュ,20","R410A","リフレッシュ",20,19.05,19.05,null,null,"LX3リフレッシュ,28","LX3","リフレッシュ",28,100]
["R410Aリフレッシュ,22","R410A","リフレッシュ",22,19.05,19.05,null,null,"LX3リフレッシュ,30","LX3","リフレッシュ",30,100]
["R410Aリフレッシュ,24","R410A","リフレッシュ",24,19.05,19.05,null,null,"LX3リフレッシュ,32","LX3","リフレッシュ",32,100]
["R410Aリフレッシュ,26","R410A","リフレッシュ",26,22.22,22.22,null,null,"LX3リフレッシュ,34","LX3","リフレッシュ",34,100]
["R410Aリフレッシュ,28","R410A","リフレッシュ",28,22.22,22.22,null,null,"LX3リフレッシュ,36","LX3","リフレッシュ",36,100]
["R410Aリフレッシュ,30","R410A","リフレッシュ",30,22.22,22.22,null,null,"LX3リフレッシュ,38","LX3","リフレッシュ",38,100]
["R410Aリフレッシュ,32","R410A","リフレッシュ",32,22.22,22.22,null,null,"LX3リフレッシュ,40","LX3","リフレッシュ",40,100]
["R410Aリフレッシュ,34","R410A","リフレッシュ",34,22.22,22.22,null,null,"LX3リフレッシュ,42","LX3","リフレッシュ",42,100]
["R410Aリフレッシュ,36","R410A","リフレッシュ",36,22.22,22.22,null,null,"LX3リフレッシュ,44","LX3","リフレッシュ",44,100]
["R410Aリフレッシュ,38","R410A","リフレッシュ",38,25.4,25.4,null,null,"LX3リフレッシュ,46","LX3","リフレッシュ",46,100]
["R410Aリフレッシュ,40","R410A","リフレッシュ",40,25.4,25.4,null,null,"LX3リフレッシュ,48","LX3","リフレッシュ",48,100]
["R410Aリフレッシュ,42","R410A","リフレッシュ",42,25.4,25.4,null,null,"LX3冷暖フリー,8","LX3","冷暖フリー",8,50,"関数でエラーを出さないため便宜上50と入力"]
["R410Aリフレッシュ,44","R410A","リフレッシュ",44,25.4,25.4,null,null,"LX3冷暖フリー,10","LX3","冷暖フリー",10,50,"関数でエラーを出さないため便宜上50と入力"]
["R410Aリフレッシュ,46","R410A","リフレッシュ",46,25.4,25.4,null,null,"LX3冷暖フリー,12","LX3","冷暖フリー",12,50,"関数でエラーを出さないため便宜上50と入力"]
["R410Aリフレッシュ,48","R410A","リフレッシュ",48,25.4,25.4,null,null,"LX3冷暖フリー,14","LX3","冷暖フリー",14,50,"マルチカタログ10年7月版108ページ"]
["R410A冷暖フリー,8","R410A","冷暖フリー",8,9.52,12.7,null,null,"LX3冷暖フリー,16","LX3","冷暖フリー",16,50]
["R410A冷暖フリー,10","R410A","冷暖フリー",10,9.52,12.7,null,null,"LX3冷暖フリー,18","LX3","冷暖フリー",18,50]
["R410A冷暖フリー,12","R410A","冷暖フリー",12,12.7,12.7,null,null,"LX3冷暖フリー,20","LX3","冷暖フリー",20,50]
["R410A冷暖フリー,14","R410A","冷暖フリー",14,12.7,12.7,null,null,"LX3冷暖フリー,22","LX3","冷暖フリー",22,50]
["R410A冷暖フリー,16","R410A","冷暖フリー",16,12.7,12.7,null,null,"LX3冷暖フリー,24","LX3","冷暖フリー",24,50]
["R410A冷暖フリー,18","R410A","冷暖フリー",18,12.7,15.88,null,null,"LX3冷暖フリー,26","LX3","冷暖フリー",26,100]
["R410A冷暖フリー,20","R410A","冷暖フリー",20,12.7,15.88,null,null,"LX3冷暖フリー,28","LX3","冷暖フリー",28,100]
["R410A冷暖フリー,22","R410A","冷暖フリー",22,12.7,15.88,null,null,"LX3冷暖フリー,30","LX3","冷暖フリー",30,100]
["R410A冷暖フリー,24","R410A","冷暖フリー",24,12.7,15.88,null,null,"LX3冷暖フリー,32","LX3","冷暖フリー",32,100]
["R410A冷暖フリー,26","R410A","冷暖フリー",26,15.88,19.05,null,null,"LX3冷暖フリー,34","LX3","冷暖フリー",34,100]
["R410A冷暖フリー,28","R410A","冷暖フリー",28,15.88,19.05,null,null,"LX3冷暖フリー,36","LX3","冷暖フリー",36,100]
["R410A冷暖フリー,30","R410A","冷暖フリー",30,15.88,19.05,null,null,"LX3冷暖フリー,38","LX3","冷暖フリー",38,100]
[{"$f":"B67&C67&\",\"&D67","v":"R410A冷暖フリー,32"},"R410A","冷暖フリー",32,15.88,19.05,null,null,{"$f":"J67&K67&\",\"&L67","v":"LX3冷暖フリー,40"},"LX3","冷暖フリー",40,100]
["R410A冷暖フリー,34","R410A","冷暖フリー",34,15.88,19.05,null,null,"LX3冷暖フリー,42","LX3","冷暖フリー",42,100]
["R410A冷暖フリー,36","R410A","冷暖フリー",36,15.88,19.05,null,null,"LX3冷暖フリー,44","LX3","冷暖フリー",44,100]
["R410A冷暖フリー,38","R410A","冷暖フリー",38,19.05,22.22,null,null,"LX3冷暖フリー,46","LX3","冷暖フリー",46,100]
["R410A冷暖フリー,40","R410A","冷暖フリー",40,19.05,22.22,null,null,"LX3冷暖フリー,48","LX3","冷暖フリー",48,100]
["R410A冷暖フリー,42","R410A","冷暖フリー",42,19.05,22.22,null,null,"LX4標準,4","LX4","標準",4,7.18]
["R410A冷暖フリー,44","R410A","冷暖フリー",44,19.05,22.22,null,null,"LX4標準,5","LX4","標準",5,7.18]
["R410A冷暖フリー,46","R410A","冷暖フリー",46,19.05,22.22,null,null,"LX4標準,6","LX4","標準",6,50,"据説記載なし：関数でエラーを出さないため便宜上50と入力"]
["R410A冷暖フリー,48","R410A","冷暖フリー",48,19.05,22.22,null,null,"LX4標準,8","LX4","標準",8,40]
[{"$f":"B76&C76&\",\"&D76","v":"R410A冷暖フリー,50"},"R410A","冷暖フリー",50,19.05,22.22,null,null,"LX4標準,10","LX4","標準",10,40]
[{"$f":"B77&C77&\",\"&D77","v":"R410A冷暖フリー,52"},"R410A","冷暖フリー",52,19.05,22.22,null,null,"LX4標準,12","LX4","標準",12,50]
[{"$f":"B78&C78&\",\"&D78","v":"R410A冷暖フリー,54"},"R410A","冷暖フリー",54,19.05,22.22,null,null,"LX4標準,14","LX4","標準",14,50]
[{"$f":"B79&C79&\",\"&D79","v":"R410A高効率,8"},"R410A","高効率",8,9.52,12.7,null,null,"LX4標準,16","LX4","標準",16,50]
["R410A高効率,10","R410A","高効率",10,9.52,12.7,null,null,"LX4標準,18","LX4","標準",18,50]
["R410A高効率,12","R410A","高効率",12,12.7,12.7,null,null,"LX4標準,20","LX4","標準",20,50]
["R410A高効率,16","R410A","高効率",16,12.7,12.7,null,null,"LX4標準,22","LX4","標準",22,50]
["R410A高効率,18","R410A","高効率",18,12.7,15.88,null,null,"LX4標準,24","LX4","標準",24,50]
["R410A高効率,20","R410A","高効率",20,12.7,15.88,null,null,"LX4標準,26","LX4","標準",26,100]
["R410A高効率,22","R410A","高効率",22,12.7,15.88,null,null,"LX4標準,28","LX4","標準",28,100]
["R410A高効率,24","R410A","高効率",24,12.7,15.88,null,null,"LX4標準,30","LX4","標準",30,100]
["R410A高効率,26","R410A","高効率",26,15.88,19.05,null,null,"LX4標準,32","LX4","標準",32,100]
["R410A高効率,28","R410A","高効率",28,15.88,19.05,null,null,"LX4標準,34","LX4","標準",34,100]
["R410A高効率,30","R410A","高効率",30,15.88,19.05,null,null,"LX4標準,36","LX4","標準",36,100]
["R410A高効率,32","R410A","高効率",32,15.88,19.05,null,null,"LX4標準,38","LX4","標準",38,100]
["R410A高効率,34","R410A","高効率",34,15.88,19.05,null,null,"LX4標準,40","LX4","標準",40,100]
["R410A高効率,36","R410A","高効率",36,15.88,19.05,null,null,"LX4標準,42","LX4","標準",42,100]
["R22標準,4","R22","標準",4,9.52,9.52,null,null,"LX4標準,44","LX4","標準",44,100]
["R22標準,5","R22","標準",5,9.52,9.52,null,null,"LX4標準,46","LX4","標準",46,100]
["R22標準,6","R22","標準",6,9.52,9.52,null,null,"LX4標準,48","LX4","標準",48,100]
["R22標準,8","R22","標準",8,12.7,12.7,null,null,"LX4標準,50","LX4","標準",50,100]
["R22標準,10","R22","標準",10,12.7,12.7,null,null,"LX4標準,52","LX4","標準",52,100]
["R22標準,13","R22","標準",13,15.88,15.88,null,null,"LX4標準,54","LX4","標準",54,100]
["R22標準,16","R22","標準",16,15.88,15.88,null,null,"LX4リフレッシュ,8","LX4","リフレッシュ",8,40]
["R22標準,20","R22","標準",20,19.05,19.05,null,null,"LX4リフレッシュ,10","LX4","リフレッシュ",10,40]
["R22標準,24","R22","標準",24,19.05,19.05,null,null,"LX4リフレッシュ,12","LX4","リフレッシュ",12,50]
["R22標準,26","R22","標準",26,22.22,22.22,null,null,"LX4リフレッシュ,14","LX4","リフレッシュ",14,50]
["R22標準,28","R22","標準",28,22.22,22.22,null,null,"LX4リフレッシュ,16","LX4","リフレッシュ",16,50]
["R22標準,30","R22","標準",30,22.22,22.22,null,null,"LX4リフレッシュ,18","LX4","リフレッシュ",18,50]
["R407C標準,4","R407C","標準",4,9.52,9.52,null,null,"LX4リフレッシュ,20","LX4","リフレッシュ",20,50]
["R407C標準,5","R407C","標準",5,9.52,9.52,null,null,"LX4リフレッシュ,22","LX4","リフレッシュ",22,50]
["R407C標準,6","R407C","標準",6,9.52,9.52,null,null,"LX4リフレッシュ,24","LX4","リフレッシュ",24,50]
["R407C標準,8","R407C","標準",8,12.7,12.7,null,null,"LX4リフレッシュ,26","LX4","リフレッシュ",26,100]
["R407C標準,10","R407C","標準",10,12.7,12.7,null,null,"LX4リフレッシュ,28","LX4","リフレッシュ",28,100]
["R407C標準,13","R407C","標準",13,15.88,15.88,null,null,"LX4リフレッシュ,30","LX4","リフレッシュ",30,100]
["R407C標準,16","R407C","標準",16,15.88,15.88,null,null,"LX4リフレッシュ,32","LX4","リフレッシュ",32,100]
["R407C標準,20","R407C","標準",20,19.05,19.05,null,null,"LX4リフレッシュ,34","LX4","リフレッシュ",34,100]
["R407C標準,24","R407C","標準",24,19.05,19.05,null,null,"LX4リフレッシュ,36","LX4","リフレッシュ",36,100]
["R407C標準,26","R407C","標準",26,22.22,22.22,null,null,"LX4リフレッシュ,38","LX4","リフレッシュ",38,100]
["R407C標準,28","R407C","標準",28,22.22,22.22,null,null,"LX4リフレッシュ,40","LX4","リフレッシュ",40,100]
["R407C標準,30","R407C","標準",30,22.22,22.22,null,null,"LX4リフレッシュ,42","LX4","リフレッシュ",42,100]
["R22冷暖フリー,8","R22","冷暖フリー",8,12.7,12.7,null,null,"LX4冷暖フリー,8","LX4","冷暖フリー",8,50]
["R22冷暖フリー,10","R22","冷暖フリー",10,12.7,12.7,null,null,"LX4冷暖フリー,10","LX4","冷暖フリー",10,50]
["R22冷暖フリー,20","R22","冷暖フリー",20,19.05,19.05,null,null,"LX4冷暖フリー,12","LX4","冷暖フリー",12,50]
[{"$f":"B120&C120&\",\"&D120","v":"R407C冷暖フリー,8"},"R407C","冷暖フリー",8,12.7,12.7,null,null,"LX4冷暖フリー,14","LX4","冷暖フリー",14,50]
[{"$f":"B121&C121&\",\"&D121","v":"R407C冷暖フリー,10"},"R407C","冷暖フリー",10,12.7,12.7,null,null,"LX4冷暖フリー,16","LX4","冷暖フリー",16,50]
[{"$f":"B122&C122&\",\"&D122","v":"R407C冷暖フリー,20"},"R407C","冷暖フリー",20,19.05,19.05,null,null,"LX4冷暖フリー,18","LX4","冷暖フリー",18,50]
[{"$f":"B123&C123&\",\"&D123","v":"R410A冷暖フリー・リフレッシュ,8"},"R410A","冷暖フリー・リフレッシュ",8,9.52,12.7,null,null,"LX4冷暖フリー,20","LX4","冷暖フリー",20,50]
[{"$f":"B124&C124&\",\"&D124","v":"R410A冷暖フリー・リフレッシュ,10"},"R410A","冷暖フリー・リフレッシュ",10,9.52,12.7,null,null,"LX4冷暖フリー,22","LX4","冷暖フリー",22,50]
["R410A冷暖フリー・リフレッシュ,12","R410A","冷暖フリー・リフレッシュ",12,12.7,12.7,null,null,"LX4冷暖フリー,24","LX4","冷暖フリー",24,50]
["R410A冷暖フリー・リフレッシュ,14","R410A","冷暖フリー・リフレッシュ",14,12.7,12.7,null,null,"LX4冷暖フリー,26","LX4","冷暖フリー",26,100]
["R410A冷暖フリー・リフレッシュ,16","R410A","冷暖フリー・リフレッシュ",16,12.7,12.7,null,null,"LX4冷暖フリー,28","LX4","冷暖フリー",28,100]
["R410A冷暖フリー・リフレッシュ,18","R410A","冷暖フリー・リフレッシュ",18,12.7,15.88,null,null,"LX4冷暖フリー,30","LX4","冷暖フリー",30,100]
["R410A冷暖フリー・リフレッシュ,20","R410A","冷暖フリー・リフレッシュ",20,12.7,15.88,null,null,"LX4冷暖フリー,32","LX4","冷暖フリー",32,100]
["R410A冷暖フリー・リフレッシュ,22","R410A","冷暖フリー・リフレッシュ",22,12.7,15.88,null,null,"LX4冷暖フリー,34","LX4","冷暖フリー",34,100]
["R410A冷暖フリー・リフレッシュ,24","R410A","冷暖フリー・リフレッシュ",24,12.7,15.88,null,null,{"$f":"J131&K131&\",\"&L131","v":"LX4冷暖フリー,36"},"LX4","冷暖フリー",36,100]
["R410A冷暖フリー・リフレッシュ,26","R410A","冷暖フリー・リフレッシュ",26,15.88,19.05,null,null,"LX4冷暖フリー,38","LX4","冷暖フリー",38,100]
["R410A冷暖フリー・リフレッシュ,28","R410A","冷暖フリー・リフレッシュ",28,15.88,19.05,null,null,"LX4冷暖フリー,40","LX4","冷暖フリー",40,100]
["R410A冷暖フリー・リフレッシュ,30","R410A","冷暖フリー・リフレッシュ",30,15.88,19.05,null,null,"LX4冷暖フリー,42","LX4","冷暖フリー",42,100]
["R410AXAIR標準,16","R410A","XAIR標準",16,15.88,19.05,null,null,"LX4冷暖フリー,44","LX4","冷暖フリー",44,100]
["R410AXAIR標準,20","R410A","XAIR標準",20,15.88,19.05,null,null,"LX4冷暖フリー,46","LX4","冷暖フリー",46,100]
["R410AXAIR標準,25","R410A","XAIR標準",25,15.88,19.05,null,null,"LX4冷暖フリー,48","LX4","冷暖フリー",48,100]
["R410AXAIR標準,32","R410A","XAIR標準",32,19.05,22.22,null,null,{"$f":"J138&K138&\",\"&L138","v":"LX4冷暖フリー,50"},"LX4","冷暖フリー",50,100]
["R410AXAIR標準,36","R410A","XAIR標準",36,19.05,22.22,null,null,{"$f":"J139&K139&\",\"&L139","v":"LX4冷暖フリー,52"},"LX4","冷暖フリー",52,100]
["R410AXAIR標準,40","R410A","XAIR標準",40,19.05,22.22,null,null,{"$f":"J140&K140&\",\"&L140","v":"LX4冷暖フリー,54"},"LX4","冷暖フリー",54,100]
["R410AXAIR標準,41","R410A","XAIR標準",41,19.05,22.22,null,null,{"$f":"J141&K141&\",\"&L141","v":"LX4高効率,8"},"LX4","高効率",8,50]
["R410AXAIR標準,45","R410A","XAIR標準",45,19.05,22.22,null,null,"LX4高効率,10","LX4","高効率",10,50]
["R410AXAIR標準,50","R410A","XAIR標準",50,19.05,22.22,null,null,"LX4高効率,12","LX4","高効率",12,50]
["R410AXAIRリニューアル,16","R410A","XAIRリニューアル",16,15.88,19.05,null,null,"LX4高効率,16","LX4","高効率",16,50]
["R410AXAIRリニューアル,20","R410A","XAIRリニューアル",20,15.88,19.05,null,null,"LX4高効率,18","LX4","高効率",18,50]
["R410AXAIRリニューアル,25","R410A","XAIRリニューアル",25,15.88,19.05,null,null,"LX4高効率,20","LX4","高効率",20,50]
["R410AXAIRリニューアル,32","R410A","XAIRリニューアル",32,19.05,22.22,null,null,"LX4高効率,22","LX4","高効率",22,50]
["R410AXAIRリニューアル,36","R410A","XAIRリニューアル",36,19.05,22.22,null,null,"LX4高効率,24","LX4","高効率",24,50]
["R410AXAIRリニューアル,40","R410A","XAIRリニューアル",40,19.05,22.22,null,null,"LX4高効率,26","LX4","高効率",26,100]
["R410AXAIRリニューアル,41","R410A","XAIRリニューアル",41,19.05,22.22,null,null,"LX4高効率,28","LX4","高効率",28,100]
["R410AXAIRリニューアル,45","R410A","XAIRリニューアル",45,19.05,22.22,null,null,"LX4高効率,30","LX4","高効率",30,100]
["R410AXAIRリニューアル,50","R410A","XAIRリニューアル",50,19.05,22.22,null,null,"LX4高効率,32","LX4","高効率",32,100]
["R410AXAIRハイパワー,16","R410A","XAIRハイパワー",16,15.88,19.05,null,null,"LX4高効率,34","LX4","高効率",34,100]
["R410AXAIRハイパワー,20","R410A","XAIRハイパワー",20,15.88,19.05,null,null,"LX4高効率,36","LX4","高効率",36,100]
["R410AXAIRハイパワー,25","R410A","XAIRハイパワー",25,15.88,19.05,null,null,"LX4冷暖フリー・リフレッシュ,8","LX4","冷暖フリー・リフレッシュ",8,50]
["R410AXAIRハイパワー,32","R410A","XAIRハイパワー",32,19.05,22.22,null,null,"LX4冷暖フリー・リフレッシュ,10","LX4","冷暖フリー・リフレッシュ",10,50]
["R410AXAIRハイパワー,36","R410A","XAIRハイパワー",36,19.05,22.22,null,null,"LX4冷暖フリー・リフレッシュ,12","LX4","冷暖フリー・リフレッシュ",12,50]
["R410AXAIRハイパワー,40","R410A","XAIRハイパワー",40,19.05,22.22,null,null,"LX4冷暖フリー・リフレッシュ,14","LX4","冷暖フリー・リフレッシュ",14,50]
["R410AXAIRハイパワー,41","R410A","XAIRハイパワー",41,19.05,22.22,null,null,"LX4冷暖フリー・リフレッシュ,16","LX4","冷暖フリー・リフレッシュ",16,50]
["R410AXAIRハイパワー,45","R410A","XAIRハイパワー",45,19.05,22.22,null,null,"LX4冷暖フリー・リフレッシュ,18","LX4","冷暖フリー・リフレッシュ",18,50]
["R410AXAIRハイパワー,50","R410A","XAIRハイパワー",50,19.05,22.22,null,null,"LX4冷暖フリー・リフレッシュ,20","LX4","冷暖フリー・リフレッシュ",20,50]
["R410AXAIRハイパワーリニューアル,16","R410A","XAIRハイパワーリニューアル",16,15.88,19.05,null,null,"LX4冷暖フリー・リフレッシュ,22","LX4","冷暖フリー・リフレッシュ",22,50]
["R410AXAIRハイパワーリニューアル,20","R410A","XAIRハイパワーリニューアル",20,15.88,19.05,null,null,"LX4冷暖フリー・リフレッシュ,24","LX4","冷暖フリー・リフレッシュ",24,50]
["R410AXAIRハイパワーリニューアル,25","R410A","XAIRハイパワーリニューアル",25,15.88,19.05,null,null,"LX4冷暖フリー・リフレッシュ,26","LX4","冷暖フリー・リフレッシュ",26,100]
["R410AXAIRハイパワーリニューアル,32","R410A","XAIRハイパワーリニューアル",32,19.05,22.22,null,null,"LX4冷暖フリー・リフレッシュ,28","LX4","冷暖フリー・リフレッシュ",28,100]
["R410AXAIRハイパワーリニューアル,36","R410A","XAIRハイパワーリニューアル",36,19.05,22.22,null,null,"LX4冷暖フリー・リフレッシュ,30","LX4","冷暖フリー・リフレッシュ",30,100]
["R410AXAIRハイパワーリニューアル,40","R410A","XAIRハイパワーリニューアル",40,19.05,22.22,null,null,{"$f":"J167&K167&\",\"&L167","v":"XAIR標準,16"},"XAIR","標準",16,100]
["R410AXAIRハイパワーリニューアル,41","R410A","XAIRハイパワーリニューアル",41,19.05,22.22,null,null,{"$f":"J168&K168&\",\"&L168","v":"XAIR標準,20"},"XAIR","標準",20,100]
["R410AXAIRハイパワーリニューアル,45","R410A","XAIRハイパワーリニューアル",45,19.05,22.22,null,null,"XAIR標準,25","XAIR","標準",25,100]
["R410AXAIRハイパワーリニューアル,50","R410A","XAIRハイパワーリニューアル",50,19.05,22.22,null,null,"XAIRリニューアル,16","XAIR","リニューアル",16,100]
["R410AECO1標準,8","R410A","ECO1標準",8,9.52,12.7,null,null,"XAIRリニューアル,20","XAIR","リニューアル",20,100]
["R410AECO1標準,10","R410A","ECO1標準",10,9.52,12.7,null,null,"XAIRリニューアル,25","XAIR","リニューアル",25,100]
["R410AECO1標準,13","R410A","ECO1標準",13,12.7,15.88,null,null,"XAIRハイパワー,16","XAIR","ハイパワー",16,100]
["R410AECO1標準小型,16","R410A","ECO1標準小型",16,12.7,15.88,null,null,"XAIRハイパワー,20","XAIR","ハイパワー",20,100]
["R410AECO1標準,16","R410A","ECO1標準",16,15.88,19.05,null,null,"XAIRハイパワー,25","XAIR","ハイパワー",25,100]
["R410AECO1標準,20","R410A","ECO1標準",20,15.88,19.05,null,null,"XAIRハイパワーリニューアル,16","XAIR","ハイパワーリニューアル",16,100]
["R410AECO1標準,25","R410A","ECO1標準",25,15.88,19.05,null,null,"XAIRハイパワーリニューアル,20","XAIR","ハイパワーリニューアル",20,100]
["R410AECO1標準,32","R410A","ECO1標準",32,19.05,22.22,null,null,"XAIRハイパワーリニューアル,25","XAIR","ハイパワーリニューアル",25,100]
["R410AECO1標準,36","R410A","ECO1標準",36,19.05,22.22,null,null,"ECO1標準,8","ECO1","標準",8,100]
["R410AECO1標準,40","R410A","ECO1標準",40,19.05,22.22,null,null,"ECO1標準,10","ECO1","標準",10,100]
["R410AECO1標準,41","R410A","ECO1標準",41,19.05,22.22,null,null,"ECO1標準,13","ECO1","標準",13,100]
["R410AECO1標準,45","R410A","ECO1標準",45,19.05,22.22,null,null,"ECO1標準,16","ECO1","標準",16,100]
["R410AECO1標準,50","R410A","ECO1標準",50,19.05,22.22,null,null,"ECO1標準,20","ECO1","標準",20,100]
["R410AECO1リニューアル,8","R410A","ECO1リニューアル",8,9.52,12.7,null,null,"ECO1標準,25","ECO1","標準",25,100]
["R410AECO1リニューアル,10","R410A","ECO1リニューアル",10,9.52,12.7,null,null,"ECO1リニューアル,8","ECO1","リニューアル",8,100]
["R410AECO1リニューアル,13","R410A","ECO1リニューアル",13,12.7,15.88,null,null,"ECO1リニューアル,10","ECO1","リニューアル",10,100]
["R410AECO1リニューアル小型,16","R410A","ECO1リニューアル小型",16,12.7,15.88,null,null,"ECO1リニューアル,13","ECO1","リニューアル",13,100]
[{"$f":"B188&C188&\",\"&D188","v":"R410AECO1リニューアル,16"},"R410A","ECO1リニューアル",16,15.88,19.05,null,null,"ECO1リニューアル,16","ECO1","リニューアル",16,100]
["R410AECO1リニューアル,20","R410A","ECO1リニューアル",20,15.88,19.05,null,null,"ECO1リニューアル,20","ECO1","リニューアル",20,100]
["R410AECO1リニューアル,25","R410A","ECO1リニューアル",25,15.88,19.05,null,null,"ECO1リニューアル,25","ECO1","リニューアル",25,100]
["R410AECO1リニューアル,32","R410A","ECO1リニューアル",32,19.05,22.22,null,null,"ECO1ハイパワー,16","ECO1","ハイパワー",16,100]
["R410AECO1リニューアル,36","R410A","ECO1リニューアル",36,19.05,22.22,null,null,"ECO1ハイパワー,20","ECO1","ハイパワー",20,100]
["R410AECO1リニューアル,40","R410A","ECO1リニューアル",40,19.05,22.22,null,null,"ECO1ハイパワー,25","ECO1","ハイパワー",25,100]
["R410AECO1リニューアル,41","R410A","ECO1リニューアル",41,19.05,22.22,null,null,"ECO1ハイパワーリニューアル,16","ECO1","ハイパワーリニューアル",16,100]
["R410AECO1リニューアル,45","R410A","ECO1リニューアル",45,19.05,22.22,null,null,"ECO1ハイパワーリニューアル,20","ECO1","ハイパワーリニューアル",20,100]
["R410AECO1リニューアル,50","R410A","ECO1リニューアル",50,19.05,22.22,null,null,"ECO1ハイパワーリニューアル,25","ECO1","ハイパワーリニューアル",25,100]
[{"$f":"B197&C197&\",\"&D197","v":"R410AECO1ハイパワー,16"},"R410A","ECO1ハイパワー",16,15.88,19.05,null,null,"XAIRⅡXAIR標準,16","XAIRⅡ","XAIR標準",16,100,"2017/12月追加"]
[{"$f":"B198&C198&\",\"&D198","v":"R410AECO1ハイパワー,20"},"R410A","ECO1ハイパワー",20,15.88,19.05,null,null,{"$f":"J198&K198&\",\"&L198","v":"XAIRⅡXAIR標準,20"},"XAIRⅡ","XAIR標準",20,100,"↑"]
[{"$f":"B199&C199&\",\"&D199","v":"R410AECO1ハイパワー,25"},"R410A","ECO1ハイパワー",25,15.88,19.05,null,null,{"$f":"J199&K199&\",\"&L199","v":"XAIRⅡXAIR標準,25"},"XAIRⅡ","XAIR標準",25,100,"↑"]
[{"$f":"B200&C200&\",\"&D200","v":"R410AECO1ハイパワー,32"},"R410A","ECO1ハイパワー",32,19.05,22.22,null,null,{"$f":"J200&K200&\",\"&L200","v":"XAIRⅡXAIR標準,30"},"XAIRⅡ","XAIR標準",30,100,"↑"]
["R410AECO1ハイパワー,36","R410A","ECO1ハイパワー",36,19.05,22.22,null,null,{"$f":"J201&K201&\",\"&L201","v":"XAIRⅡXAIR標準,32"},"XAIRⅡ","XAIR標準",32,100,"↑"]
["R410AECO1ハイパワー,40","R410A","ECO1ハイパワー",40,19.05,22.22,null,null,"XAIRⅡXAIR標準,36","XAIRⅡ","XAIR標準",36,100,"↑"]
["R410AECO1ハイパワー,41","R410A","ECO1ハイパワー",41,19.05,22.22,null,null,"XAIRⅡXAIR標準,40","XAIRⅡ","XAIR標準",40,100,"↑"]
["R410AECO1ハイパワー,45","R410A","ECO1ハイパワー",45,19.05,22.22,null,null,"XAIRⅡXAIR標準,45","XAIRⅡ","XAIR標準",45,100,"↑"]
["R410AECO1ハイパワー,50","R410A","ECO1ハイパワー",50,19.05,22.22,null,null,"XAIRⅡXAIR標準,50","XAIRⅡ","XAIR標準",50,100,"↑"]
["R410AECO1ハイパワーリニューアル,16","R410A","ECO1ハイパワーリニューアル",16,15.88,19.05,null,null,"XAIRⅡXAIR標準,55","XAIRⅡ","XAIR標準",55,100,"↑"]
["R410AECO1ハイパワーリニューアル,20","R410A","ECO1ハイパワーリニューアル",20,15.88,19.05,null,null,"XAIRⅡXAIR標準,60","XAIRⅡ","XAIR標準",60,100,"↑"]
["R410AECO1ハイパワーリニューアル,25","R410A","ECO1ハイパワーリニューアル",25,15.88,19.05,null,null,{"$f":"J208&K208&\",\"&L208","v":"XAIRⅡXAIRリニューアル,16"},"XAIRⅡ","XAIRリニューアル",16,100,"↑"]
["R410AECO1ハイパワーリニューアル,32","R410A","ECO1ハイパワーリニューアル",32,19.05,22.22,null,null,{"$f":"J209&K209&\",\"&L209","v":"XAIRⅡXAIRリニューアル,20"},"XAIRⅡ","XAIRリニューアル",20,100,"↑"]
["R410AECO1ハイパワーリニューアル,36","R410A","ECO1ハイパワーリニューアル",36,19.05,22.22,null,null,{"$f":"J210&K210&\",\"&L210","v":"XAIRⅡXAIRリニューアル,25"},"XAIRⅡ","XAIRリニューアル",25,100,"↑"]
["R410AECO1ハイパワーリニューアル,40","R410A","ECO1ハイパワーリニューアル",40,19.05,22.22,null,null,{"$f":"J211&K211&\",\"&L211","v":"XAIRⅡXAIRリニューアル,30"},"XAIRⅡ","XAIRリニューアル",30,100,"↑"]
["R410AECO1ハイパワーリニューアル,41","R410A","ECO1ハイパワーリニューアル",41,19.05,22.22,null,null,{"$f":"J212&K212&\",\"&L212","v":"XAIRⅡXAIRリニューアル,32"},"XAIRⅡ","XAIRリニューアル",32,100,"↑"]
["R410AECO1ハイパワーリニューアル,45","R410A","ECO1ハイパワーリニューアル",45,19.05,22.22,null,null,"XAIRⅡXAIRリニューアル,36","XAIRⅡ","XAIRリニューアル",36,100,"↑"]
["R410AECO1ハイパワーリニューアル,50","R410A","ECO1ハイパワーリニューアル",50,19.05,22.22,null,null,"XAIRⅡXAIRリニューアル,40","XAIRⅡ","XAIRリニューアル",40,100,"↑"]
["R410AXAIR標準,16","R410A","XAIR標準",16,15.88,19.05,"XAIRⅡ",null,"XAIRⅡXAIRリニューアル,45","XAIRⅡ","XAIRリニューアル",45,100,"↑"]
["R410AXAIR標準,20","R410A","XAIR標準",20,15.88,19.05,"↑",null,"XAIRⅡXAIRリニューアル,50","XAIRⅡ","XAIRリニューアル",50,100,"↑"]
["R410AXAIR標準,25","R410A","XAIR標準",25,15.88,19.05,"↑",null,"XAIRⅡXAIRリニューアル,55","XAIRⅡ","XAIRリニューアル",55,100,"↑"]
["R410AXAIR標準,30","R410A","XAIR標準",30,19.05,22.22,"↑",null,"XAIRⅡXAIRリニューアル,60","XAIRⅡ","XAIRリニューアル",60,100,"↑"]
["R410AXAIR標準,32","R410A","XAIR標準",32,19.05,22.22,"↑",null,{"$f":"J219&K219&\",\"&L219","v":"XAIRⅡXAIRハイパワー,16"},"XAIRⅡ","XAIRハイパワー",16,100,"↑"]
["R410AXAIR標準,36","R410A","XAIR標準",36,19.05,22.22,"↑",null,{"$f":"J220&K220&\",\"&L220","v":"XAIRⅡXAIRハイパワー,20"},"XAIRⅡ","XAIRハイパワー",20,100,"↑"]
["R410AXAIR標準,40","R410A","XAIR標準",40,19.05,22.22,"↑",null,{"$f":"J221&K221&\",\"&L221","v":"XAIRⅡXAIRハイパワー,25"},"XAIRⅡ","XAIRハイパワー",25,100,"↑"]
["R410AXAIR標準,45","R410A","XAIR標準",45,19.05,22.22,"↑",null,{"$f":"J222&K222&\",\"&L222","v":"XAIRⅡXAIRハイパワー,30"},"XAIRⅡ","XAIRハイパワー",30,100,"↑"]
["R410AXAIR標準,50","R410A","XAIR標準",50,19.05,22.22,"↑",null,{"$f":"J223&K223&\",\"&L223","v":"XAIRⅡXAIRハイパワー,32"},"XAIRⅡ","XAIRハイパワー",32,100,"↑"]
["R410AXAIR標準,55","R410A","XAIR標準",55,22.22,22.22,"↑",null,"XAIRⅡXAIRハイパワー,36","XAIRⅡ","XAIRハイパワー",36,100,"↑"]
["R410AXAIR標準,60","R410A","XAIR標準",60,22.22,22.22,"↑",null,"XAIRⅡXAIRハイパワー,40","XAIRⅡ","XAIRハイパワー",40,100,"↑"]
["R410AXAIRリニューアル,16","R410A","XAIRリニューアル",16,15.88,19.05,"↑",null,"XAIRⅡXAIRハイパワー,45","XAIRⅡ","XAIRハイパワー",45,100,"↑"]
["R410AXAIRリニューアル,20","R410A","XAIRリニューアル",20,15.88,19.05,"↑",null,"XAIRⅡXAIRハイパワー,50","XAIRⅡ","XAIRハイパワー",50,100,"↑"]
["R410AXAIRリニューアル,25","R410A","XAIRリニューアル",25,15.88,19.05,"↑",null,"XAIRⅡXAIRハイパワー,55","XAIRⅡ","XAIRハイパワー",55,100,"↑"]
["R410AXAIRリニューアル,30","R410A","XAIRリニューアル",30,19.05,22.22,"↑",null,"XAIRⅡXAIRハイパワー,60","XAIRⅡ","XAIRハイパワー",60,100,"↑"]
["R410AXAIRリニューアル,32","R410A","XAIRリニューアル",32,19.05,22.22,"↑",null,{"$f":"J230&K230&\",\"&L230","v":"XAIRⅡXIARハイパワーリニューアル,16"},"XAIRⅡ","XIARハイパワーリニューアル",16,100,"↑"]
["R410AXAIRリニューアル,36","R410A","XAIRリニューアル",36,19.05,22.22,"↑",null,{"$f":"J231&K231&\",\"&L231","v":"XAIRⅡXIARハイパワーリニューアル,20"},"XAIRⅡ","XIARハイパワーリニューアル",20,100,"↑"]
["R410AXAIRリニューアル,40","R410A","XAIRリニューアル",40,19.05,22.22,"↑",null,{"$f":"J232&K232&\",\"&L232","v":"XAIRⅡXIARハイパワーリニューアル,25"},"XAIRⅡ","XIARハイパワーリニューアル",25,100,"↑"]
["R410AXAIRリニューアル,45","R410A","XAIRリニューアル",45,19.05,22.22,"↑",null,{"$f":"J233&K233&\",\"&L233","v":"XAIRⅡXIARハイパワーリニューアル,30"},"XAIRⅡ","XIARハイパワーリニューアル",30,100,"↑"]
["R410AXAIRリニューアル,50","R410A","XAIRリニューアル",50,19.05,22.22,"↑",null,{"$f":"J234&K234&\",\"&L234","v":"XAIRⅡXAIRハイパワーリニューアル,32"},"XAIRⅡ","XAIRハイパワーリニューアル",32,100,"↑"]
["R410AXAIRリニューアル,55","R410A","XAIRリニューアル",55,22.22,22.22,"↑",null,"XAIRⅡXAIRハイパワーリニューアル,36","XAIRⅡ","XAIRハイパワーリニューアル",36,100,"↑"]
["R410AXAIRリニューアル,60","R410A","XAIRリニューアル",60,22.22,22.22,"↑",null,"XAIRⅡXAIRハイパワーリニューアル,40","XAIRⅡ","XAIRハイパワーリニューアル",40,100,"↑"]
["R410AXAIRハイパワー,16","R410A","XAIRハイパワー",16,15.88,19.05,"↑",null,"XAIRⅡXAIRハイパワーリニューアル,45","XAIRⅡ","XAIRハイパワーリニューアル",45,100,"↑"]
["R410AXAIRハイパワー,20","R410A","XAIRハイパワー",20,15.88,19.05,"↑",null,"XAIRⅡXAIRハイパワーリニューアル,50","XAIRⅡ","XAIRハイパワーリニューアル",50,100,"↑"]
["R410AXAIRハイパワー,25","R410A","XAIRハイパワー",25,15.88,19.05,"↑",null,"XAIRⅡXAIRハイパワーリニューアル,55","XAIRⅡ","XAIRハイパワーリニューアル",55,100,"↑"]
["R410AXAIRハイパワー,30","R410A","XAIRハイパワー",30,19.05,22.22,"↑",null,"XAIRⅡXAIRハイパワーリニューアル,60","XAIRⅡ","XAIRハイパワーリニューアル",60,100,"↑"]
["R410AXAIRハイパワー,32","R410A","XAIRハイパワー",32,19.05,22.22,"↑",null,"LX5標準,10","LX5","標準",10,50,"↑"]
["R410AXAIRハイパワー,36","R410A","XAIRハイパワー",36,19.05,22.22,"↑",null,"LX5標準,12","LX5","標準",12,50,"↑"]
["R410AXAIRハイパワー,40","R410A","XAIRハイパワー",40,19.05,22.22,"↑",null,"LX5標準,14","LX5","標準",14,50,"↑"]
["R410AXAIRハイパワー,45","R410A","XAIRハイパワー",45,19.05,22.22,"↑",null,"LX5標準,16","LX5","標準",16,50,"↑"]
["R410AXAIRハイパワー,50","R410A","XAIRハイパワー",50,19.05,22.22,"↑",null,"LX5標準,18","LX5","標準",18,50,"↑"]
["R410AXAIRハイパワー,55","R410A","XAIRハイパワー",55,22.22,22.22,"↑",null,"LX5標準,20","LX5","標準",20,50,"↑"]
["R410AXAIRハイパワー,60","R410A","XAIRハイパワー",60,22.22,22.22,"↑",null,"LX5標準,20","LX5","標準",20,50,"↑"]
["R410AXIARハイパワーリニューアル,16","R410A","XIARハイパワーリニューアル",16,15.88,19.05,"↑",null,"LX5標準,22","LX5","標準",22,50,"↑"]
["R410AXIARハイパワーリニューアル,20","R410A","XIARハイパワーリニューアル",20,15.88,19.05,"↑",null,"LX5標準,24","LX5","標準",24,50,"↑"]
["R410AXIARハイパワーリニューアル,25","R410A","XIARハイパワーリニューアル",25,15.88,19.05,"↑",null,"LX5標準,26","LX5","標準",26,100,"↑"]
["R410AXIARハイパワーリニューアル,30","R410A","XIARハイパワーリニューアル",30,19.05,22.22,"↑",null,"LX5標準,28","LX5","標準",28,100,"↑"]
["R410AXAIRハイパワーリニューアル,32","R410A","XAIRハイパワーリニューアル",32,19.05,22.22,"↑",null,"LX5標準,30","LX5","標準",30,100,"↑"]
["R410AXAIRハイパワーリニューアル,36","R410A","XAIRハイパワーリニューアル",36,19.05,22.22,"↑",null,"LX5標準,32","LX5","標準",32,100,"↑"]
["R410AXAIRハイパワーリニューアル,40","R410A","XAIRハイパワーリニューアル",40,19.05,22.22,"↑",null,"LX5標準,34","LX5","標準",34,100,"↑"]
["R410AXAIRハイパワーリニューアル,45","R410A","XAIRハイパワーリニューアル",45,19.05,22.22,"↑",null,"LX5標準,36","LX5","標準",36,100,"↑"]
[{"$f":"B256&C256&\",\"&D256","v":"R410AXAIRハイパワーリニューアル,50"},"R410A","XAIRハイパワーリニューアル",50,19.05,22.22,"↑",null,"LX5標準,38","LX5","標準",38,100,"↑"]
[{"$f":"B257&C257&\",\"&D257","v":"R410AXAIRハイパワーリニューアル,55"},"R410A","XAIRハイパワーリニューアル",55,22.22,22.22,"↑",null,"LX5標準,40","LX5","標準",40,100,"↑"]
[{"$f":"B258&C258&\",\"&D258","v":"R410AXAIRハイパワーリニューアル,60"},"R410A","XAIRハイパワーリニューアル",60,22.22,22.22,"↑",null,"LX5標準,38","LX5","標準",38,100,"↑"]
["R410A標準,10","R410A","標準",10,9.52,12.7,"LX5",null,"LX5標準,40","LX5","標準",40,100,"↑"]
["R410A標準,12","R410A","標準",12,12.7,12.7,"↑",null,"LX5標準,42","LX5","標準",42,100,"↑"]
["R410A標準,14","R410A","標準",14,12.7,12.7,"↑",null,"LX5標準,44","LX5","標準",44,100,"↑"]
["R410A標準,16","R410A","標準",16,12.7,12.7,"↑",null,"LX5標準,46","LX5","標準",46,100,"↑"]
["R410A標準,18","R410A","標準",18,12.7,15.88,"↑",null,"LX5標準,48","LX5","標準",48,100,"↑"]
[{"$f":"B264&C264&\",\"&D264","v":"R410A標準,20"},"R410A","標準",20,12.7,15.88,"↑",null,"LX5標準,50","LX5","標準",50,100,"↑"]
["R410A標準,20","R410A","標準",20,12.7,15.88,"↑",null,"LX5標準,52","LX5","標準",52,100,"↑"]
["R410A標準,22","R410A","標準",22,12.7,15.88,"↑",null,"LX5標準,54","LX5","標準",54,100,"↑"]
["R410A標準,24","R410A","標準",24,12.7,15.88,"↑",null,","]
["R410A標準,26","R410A","標準",26,15.88,19.05,"↑",null,","]
["R410A標準,28","R410A","標準",28,15.88,19.05,"↑",null,","]
["R410A標準,30","R410A","標準",30,15.88,19.05,"↑",null,","]
["R410A標準,32","R410A","標準",32,15.88,19.05,"↑",null,","]
["R410A標準,34","R410A","標準",34,15.88,19.05,"↑",null,","]
["R410A標準,36","R410A","標準",36,15.88,19.05,"↑",null,","]
["R410A標準,38","R410A","標準",38,19.05,22.22,"↑",null,","]
["R410A標準,40","R410A","標準",40,19.05,22.22,"↑",null,","]
["R410A標準,38","R410A","標準",38,19.05,22.22,"↑",null,","]
["R410A標準,40","R410A","標準",40,19.05,22.22,"↑",null,","]
["R410A標準,42","R410A","標準",42,19.05,22.22,"↑",null,","]
["R410A標準,44","R410A","標準",44,19.05,22.22,"↑",null,","]
["R410A標準,46","R410A","標準",46,19.05,22.22,"↑"]
["R410A標準,48","R410A","標準",48,19.05,22.22,"↑"]
["R410A標準,50","R410A","標準",50,19.05,22.22,"↑"]
["R410A標準,52","R410A","標準",52,19.05,22.22,"↑"]
["R410A標準,54","R410A","標準",54,19.05,22.22,"↑"]
[","]
[","]
[","]
[","]
[","]
[","]
[","]
[","]
[","]
[","]
[","]
[","]